Radford Army Ammunition Plant

Facilities, Infrastructure and Equipment -      Maintenance Technical Exhibit (A)

11/13/2024

Table of Contents

1.1.	Overview	8

1.1.1.	Workload Requirement	8

1.1.2.	Installed Building Equipment (IBE)	8

1.1.3.	Diagnosis and Analysis	9

1.2.	Components	9

1.2.15.	Caulking around windows and doors	10

1.2.16.	Painting exterior building surfaces	10

1.2.17.	Rail, Bridges, Dams, Reservoirs, Roads (ADTIP)	10

1.2.18.	Water Treatment Plants	10

1.2.19.	Water Distribution Infrastructure	10

1.2.20.	Electrical Infrastructure	10

1.2.21.	Lightning Protection Systems (LPS)	10

1.3.	Work Management and Control	10

1.3.1.	Reporting Requirements	10

1.3.1.1.	RFAAP Maintenance Plan	10

1.3.2.	Inspections	11

1.3.3.	Publications and Forms	11

1.3.4.	Key Performance Indicators (KPI).	11

2.	Equipment Maintenance - Personal Property.	12

2.2.	Mechanical Integrity	12

2.3.	Preventive Maintenance	12

2.4.	Operator Checklists.	13

2.5.	Spare and Repair Parts Program	13

2.6.	Life Cycle Cost Analysis	14

2.7.	Key Performance Indicator (KPI) Report	14

2.8.	Eye Washes and Safety Showers	14

3.	Facility Maintenance – Real Property	14

3.6.	Heating, Ventilation, and Air Conditioning (HVAC)	16

3.6.2.	Seasonal Changeover Requirements	18

3.6.4.	Related Components and Accessories	19

3.7.	Roof Maintenance	19

3.8.	Roof Gutters, Drains, and Downspouts	19

3.9.	Automatic Doors	20

3.10.	Overhead and Personnel Doors	20

3.11.	Gates, Fences, Barriers and Dock Levelers	20

3.12.	Air Compressors/Unfired Pressure Vessels	20

3.13.	Plumbing	21

3.14.	Industrial Wastewater Treatment Plant (IWTP)	22

3.15.	Heating/Cooling Plants	23

3.16.	Winterization and De-Winterization (Mothballed Buildings)	24

3.17.	Lift Stations	27

3.18.	Sedimentation Tanks Maintenance	27

3.19.	Electrical.	27

3.20.	Auxiliary Generators	27

3.21.	Grounding Points, Lightning Protection, and Cathodic Protection Maintenance	28

3.22.	Fire Alarm, Fire Suppression and building Mass Notification Systems	29

3.22.2.	Sprinkler and Hood Suppression Systems	30

3.23.	Elevator Maintenance.	30

3.24.	Elevator Inspection and Certification	30

3.25.	Keys and Locks	32

3.26.	Food Service Equipment (FSE)	33

3.26.1.	General	33

3.27.	Crane and Load Scales Maintenance and Load Testing	33

3.27.1.	General	33

3.27.2.	Preventive Maintenance Plan	33

3.27.3.	Crane Operator Training	34

3.27.4.	Load scales	34

3.28.	Glass, Glazing and Asbestos	34

4.	Operation and Maintenance of Energy Conservation Systems.	34

5.	Sign Shop Operations	36

6.	Utility Systems	37

7.	Area Lighting	38

8.	Utility Marking	39

9.	Pumps and Pumping Stations	39

11.	Propane Tanks and Distribution Systems	40

12.	Water Distribution Systems	41

13.	Storm Water Collection System	44

15.	Fuel Storage and Distribution Systems	47

16.	Water Standpipes	47

17.	Fire Loop System Hydrants	47

18.	Army Dams, Transportation and Infrastructure (ADTIP)	48

18.1.	Railroads.	48

18.2.	Bridges	48

18.3.	Vehicles	48

19.	Applicable Directives, Publications.	49

- General Information.

  - Overview.  The Contractor shall inspect, repair, and maintain all existing active buildings, structures, and their components.  This includes both the Main Plant (Montgomery/Pulaski Country) and the New River Unit (Dublin), covering 6,901 acres in total. The Contractor shall provide sustainment of vertical facilities such as buildings and all utilities plant structures within the five (5) foot demarcation line, excluding Army Family Housing.  The Contractor will coordinate with HQ, JMC-Environmental Division, if within Historic District. The contractor shall inspect, repair, and maintain all existing Personal Property to include all Industrial Machinery and Equipment, Scientific Equipment, Information Technology, Office equipment/furniture, and any other property not considered to be real property under 41 CFR Chapter 102-71.  If at any point this document contradicts language of another PWS (Environmental, Energy and Utilities, Safety, Fire) the more stringent and/or most up to date language will be used.

    - Workload Requirement. The following paragraphs describe all facets involved in the management of building and structure maintenance; they include terms used to classify work; provide information on the level of effort that will be required at Radford Army Ammunition Plant (RFAAP) in terms of workload and trade distributions; and describe the way in which work will be received, managed, and documented. The Contractor is responsible for the maintenance and repair of all active building and structures.  Under this contract the basis for the real property square footage will have a deviation of +/-5% for each type of category code without affecting the contract cost. This will allow for the addition of new facilities and for removal of existing ones without having to issue a formal modification. Work may include carpentry, plumbing, electrical, masonry, painting, sign work, HVAC work, flooring, minor roofing, metalwork, locksmith services, fire alarms, fire suppression, glass and glazing, demolition and other trades that relate to the maintenance and repair of real property facilities. The Contractor shall perform Preventive Maintenance Orders (PMOs), Corrective Maintenance Orders (CMOs), and Emergency Maintenance Orders (EMOs) on all active real property. All work requests/orders shall contain the following information at a minimum:

- Facility Fac Code, RPUID or Asset Number

- Work Description

- Customer/Requester Information

- POC Phone Number

- OEM or Operation and Maintenance Guidance

- Impact to Operation or Equipment/Structure

- Work to be performed by: inhouse/subcontract

- Estimated Start

- Estimated Completion

    - Installed Building Equipment (IBE). There is a wide variety of facilities at RFAAP with a wide variety of installed equipment. Although other sections of this Technical Exhibit detail the requirements for some of these types of equipment, all real property IBE is the responsibility of the Contractor.  DA PAM 420-11 Project Definition and Work Classification identifies installed building equipment that is covered under this contract.  Any existing equipment found after initial deliverable will be added to the CMMS inventory and maintained at no additional cost to the government.

    - Diagnosis and Analysis. The Contractor shall provide follow-up analysis and diagnosis of equipment failure as requested or shown in section 1.1.3.2.

      - The primary aim is to identify the factors that contributed to and/or resulted in the failure of maintenance, service, repair and/or operation of real property, infrastructure, personal property, and systems at RFAAP, and to identify and implement actions to prevent repeated future failure due to the same failure reasons. The Contractor shall:

a.	Provide a detailed description and explanation of the failure

b.	Identify the root cause or causes of the problem

c.	Provide possible actions and solutions to prevent future occurrences, an explanation of the pros and cons of these actions, a cost analysis of these actions, and the Contractor’s recommended action

d.	The selection and implementation of the appropriate action

e.	Review, documentation, and analysis of the outcome

f.	Change in procedures, training, PWS, etc. as needed

      - The Contractor shall provide additional analysis or diagnosis when:

a.	After catastrophic, unusual, or unforeseen events that result in adverse maintenance, repair, and service requirements

b.	When notified of unsatisfactory performance by Contracting Officer (ACO/PCO), Contracting Officers Representative (COR), HQ, JMC or other Regulatory Agencies (Safety, Occupational Safety and Health Administration (OSHA), Industrial Hygiene, Directorate of Emergency Services (DES), etc.)

c.	After any unplanned stoppage, outage, or failure of a Utility system or major utility system component. Refer to Energy and Utilities PWS for specific guidance.

  - Components.  The Contractor shall perform preventive maintenance (PM) and repairs.  Facilities and Equipment covered under this Technical Exhibit (TE)include, but are not limited to, the following:

    - Administrative Buildings

    - Training Shops

    - Maintenance Shops

    - DEMIL Facilities

    - Warehouses

    - Ammunition Storage Buildings

    - Medical Facilities and Clinics (alarms/fire systems)

    - Schools, Chapels, and recreational Facilities

    - Dining Facilities

    - Range Facilities

    - HVAC Systems

    - Fire Alarms

    - Roofs, Flashing, and Fascia

    - Installed Building Equipment

    - Caulking around windows and doors

    - Painting exterior building surfaces

    - Rail, Bridges, Dams, Reservoirs, Roads (ADTIP)

    - Water Treatment Plants

    - Water Distribution Infrastructure

    - Electrical Infrastructure

    - Lightning Protection Systems (LPS)

  - Work Management and Control.

    - Reporting Requirements.  The Contractor shall prepare and maintain all maintenance activities, records, files, and reports in a Computer-aided Maintenance Management System (CMMS).  CMMS modules and data fields shall be both searchable and exportable and describe in detail 100% of maintenance activities, to include Corrective, Preventive, Predictive and subcontracted work.  Contractor will provide a minimum of two (2) read only access points to CMMS for RFAAP government staff.

      - RFAAP Maintenance Plan.  Within thirty (30) calendar days of the start of the contract, the Contractor shall submit to the ACO/PCO/COR a RFAAP Maintenance Plan (CDRL A07-01) organized by Functional Area at minimum to include all active facilities, installed building equipment (IBE) and scheduled maintenance task frequency.  Additional Personal property equipment requirements can be found in Section 19 of this document.  The RFAAP Maintenance Plan shall describe all preventive maintenance services to be performed and their frequencies as reflected by this Contract, standard operating procedures/orders, and OEM recommendations. The following plans shall be submitted as part of the Service Plan.

        - Emergency Operating Plan. The Contractor shall provide an Emergency Operating Plan detailing how the Contractor proposes to utilize their personnel, materials, and equipment to respond to and accomplish emergency maintenance or repair work during all regular and non-regular duty hours for any utility outages. The Emergency Operating Plan shall include a procedure to follow in the event that electrical power to buildings or portions thereof is lost; a procedure to follow in the event of a water supply emergency due to interior or exterior secondary water distribution line ruptures, freeze-ups, or contamination of the water supply; a procedure to follow in the event of a natural gas or propane emergency; a procedure to follow in the event that the Installation sewage collection systems malfunction due to stoppage in the collection mains, failure of sewage lift stations, or a pipeline rupture; and include a procedure to follow in the event of a Uninterruptible Power Supply (UPS) or Emergency Generator outage or breakdown. The plan shall outline a contingency plan for providing repair, replacement, or backup power sources such as rental units during the outage or breakdown.

        - Other Emergency Services to include, but not limited to:

- Pest Control

- Natural Disasters

- Emergency work due to loss of operation of generators and water pumps

- Emergency work for the security or protection of Government Property

- Emergency work due to loss of air conditioning or heating for data processing equipment and other temperature critical facilities

- Emergency work due to a malfunction in fire alarm or fire sprinkler systems

- Response to emergency DMOs

    - Inspections.  Specific publications and forms required for the accomplishment of inspections described in this service are listed in Section 20 of this document.  Required Inspections can be found within this document organized by Functional Area at minimum and includes all active facilities, installed building equipment, industrial equipment and required rail, dams, and bridge inspections. The functional areas describe all inspections to be performed, and their frequencies as reflected by this Contract.

    - Publications and Forms.  Specific publications and forms required for the accomplishment of work described in this service are listed in Section 20 of this document.

    - Key Performance Indicators (KPI).  The KPI Report shall demonstrate efficiencies, trends, and areas requiring improvement for maintenance work performed at RFAAP and shall be submitted monthly and report the following KPIs (CDRL A07-05)

      - Backlog on Corrective Maintenance WO by Type

      - Backlog of Preventive Maintenance (in given month and overall backlog)

        - Acceptable performance threshold 95% completion rate

      - Water Break Data (completed and reported)

      - Steam Leak Data (completed and reported)

      - Mean Time to Repair (MTTR) by WO type

      - Planned Maintenance Percentage

        - Acceptable performance threshold 90% planned

      - Schedule Compliance (percentage of assigned WO’s completed as scheduled)

        - Acceptable performance threshold 97% completed as scheduled

      - Estimated vs. Actual Hours for all completed WO’s

      - Work Utilization Percentage (downtime during CM/PM/other)

      - Inventory Accuracy within CMMS

        - Acceptable performance threshold 98% accurate

## Equipment Maintenance - Personal Property.

  - The Contractor shall perform preventive maintenance, inspect, and repair all personal property.  Personal Property incudes but is not limited to: Industrial Machinery and Equipment, Scientific Equipment, Information Technology, Office equipment/furniture, and any other property not considered to be real property under 41 CFR Chapter 102-71.

## Mechanical Integrity

    - The contractor shall maintain and inspect equipment in all explosive, propellant, and pyrotechnic operations IAW 29 CFR 1910.119 Process Safety Management of Highly Hazardous Chemicals.

    - The contractor shall maintain and inspect equipment in all explosive, propellant, and pyrotechnic operations IAW the Safety PWS requirements for 29 CFR 1910.119 for Process Safety Management of Highly Hazardous Chemicals.

## Preventive Maintenance

    - Preventive Maintenance (PM) of personal property refers to regularly scheduled inspections, tests, and other maintenance activities preformed.  These activities are designed to identify and address potential problems before they can cause equipment breakdowns or downtime, disrupting production and negatively impacting the business. Preventive Maintenance activities are not to be revised, generated, or inactivated without the approval of JMC government staff.

    - Personal Property PM Plan.  Contractor shall provide in detail the strategy and procedures for inspections, testing and PMs to ensure outages due to maintenance are scheduled to minimize impact on operations Maintenance Deliverable (CDRL A07-01).  All inspections, testing and PMs will follow OEM standards and recommendations when available.  If the contractor sees benefit to deviate from OEM recommendations, they must provide proper justification to ACO/PCO and receive RFAAP staff approval prior to any deviation. (i.e time-based, usage based, or condition based predictive maintenance strategies) When OEM recommendation and standards are not available best industry standards will be used.

    - Operator checklists are daily checks completed by the equipment operator to ensure that the equipment is in good working order prior to operation.  Current active days physical checklist shall be kept at the equipment and replaced at the time of the next operator check.  Historical record of operator checklist shall be recorded into the contractors CMMS and be provided to the government upon request.  Checks shall include Serial/ equipment number, name of operator, and date/time in addition to the following at a minimum when applicable:

## Operator Checklists.

    - Operator checklists are daily checks completed by the equipment operator to ensure that the equipment is in good working order prior to operation.  Current active days physical checklist shall be kept at the equipment and replaced at the time of the next operator check.  Historical record of operator checklist shall be recorded into the contractors CMMS and be provided to the government upon request.  Checks shall include Serial/ equipment number, name of operator, and date/time in addition to the following at a minimum when applicable:

      - Check for leaks and wear in hoses and electrical conduit

      - Check oil and coolant reservoirs for proper operating levels.  Be alert to reservoirs that never require filling, excessive leaks, etc.

      - Check all pressure gauges that have marked operating levels to ensure proper operation.  If pressure gauges are found to be unmarked it will be noted on the checklist and a WO shall be generated to mark proper levels.

      - Check all filter conditions that may impede operations for excessive oil, dirt, and debris.

      - Check hydraulic or oil pumps for overheating, and report any that are noisy or hot to the touch.

## Spare and Repair Parts Program

    - The Contractor will develop and maintain a comprehensive Spare and Repair Parts Program for RFAAP that includes 100% of spare and repair parts for Government furnished property at RFAAP.

    - The Spare and Repair Parts Program shall include a list of Mission Essential Assets (MEA), prioritized based on criticality, life expectancy, and/or redundancy. The Spare and Repair Parts Program shall include stock of spare parts for all MEAs or a contingency plan that mitigates downtime if the MEA were to fail.

    - The MEA List shall be submitted within 30 calendar days of Contract Award (CDRL A07-10).  The MEA List shall be resubmitted quarterly, highlighting any changes since the previous submission (e.g. assets added, assets removed, obsolete parts and their replacements, new contingency plans, etc.).

    - The Spare and Repair Parts Program shall demonstrate effectiveness by identifying trends and areas of improvement through tracking of KPIs

## Life Cycle Cost Analysis

    - The Contractor shall conduct quarterly Life Cycle Cost Analysis (LCCA) for Mission Essential Assets (MEA). The data shall be processed as independent quarters of the year (i.e. not the aggregate YTD data).

    - The LCCA shall, at a minimum, include life cycle costs of the top 25 MEAs with the largest associated repair costs. (CDRL A07-02) Life cycle costs include cost for replacement parts, direct labor, subcontractor, and estimated lost cost from production downtime per MEA.

    - The LCCA shall include assessments for each specific quarter and total costs for the lifespan of the MEA starting at contract award.  For example, if the contract starts on 1 Jan 2027, the total costs for packaged boiler #1 would be all replacement parts, labor, subcontractor costs and lost cost from production downtime from 1 Jan 2027 to the time of CDRL submission.

## Key Performance Indicator (KPI) Report

    - The monthly KPI Report shall demonstrate efficiencies of maintenance work performed at RFAAP by tracking the following KPIs.

    - The

      - Backlog of Corrective Maintenance Work Orders by Trade

      - Backlog of Preventive Maintenance Orders (in given month and overall backlog)

        - Acceptable performance threshold 95% completion rate

      - Water Break Data (completed and reported)

      - Steam Leak Data (completed and reported)

      - Mean Time to Repair (MTTR) by WO type

      - Planned Maintenance Percentage

        - Acceptable performance threshold 90% planned

      - Schedule Compliance (percentage of assigned WO’s completed as scheduled)

        - Acceptable performance threshold 97% completed as scheduled

      - Estimated vs. Actual Hours for all completed WO’s

      - Work Utilization Percentage (downtime during CM/PM/other)

      - Inventory Accuracy within CMMS

        - Acceptable performance threshold 98% accurate

    - When KPIs are trending negative or consistently below target (for at least three consecutive months), the Contractor shall provide a plan for getting the KPI back on track.

  - Eye Washes and Safety Showers.  The Contractor shall perform Preventive and Corrective Maintenance to the eye washes and safety showers.

- Facility Maintenance – Real Property.  The Contractor shall develop and submit to (after KO approval) a Comprehensive PM and Repair Program.  PM consists primarily of inspection, cleaning, lubrication, adjustment, calibration, and minor part and component replacement on building and structures, its component equipment and other systems included at facilities.  The Contractor shall submit the Comprehensive PM and Repair Program for this service as part of (CDRL A07-01), RFAAP Maintenance Plan.  Work that is outside the scope of preventive maintenance shall be accomplished through a Work Order (WO).

    - BUILDER Sustainment Management System (SMS). BUILDER SMS is a web-based asset lifecycle management software tool created by the Engineer Research Development Center – Construction Engineering Research Laboratory of the US Army Corps of Engineers (USACE-ERDC-CERL). The Contractor shall collect, update, and maintain facility data IAW JMC BUILDER Sustainment Guide Technical Exhibit B.

  - Grounds Maintenance Site Plan. The Contractor shall provide a Grounds Maintenance Site Plan with the grounds maintenance services described herein. A description and classification (Improved, semi-improved, unimproved) of the areas to receive grounds maintenance services shall be included in the Grounds Maintenance Site Plan. Any equipment (including waste containers) moved while performing basic services shall be returned to their original position. (CDRL A07-01) .

  - Mowing.  The Contractor shall All grass cutting equipment will arrive at the site with mowing blades in a sharp condition. Mowing shall include areas identified in the contractor supplied and government approved site map included in the Grounds Maintenance Site Plan (CDRL A07-07). Routine policing of the grounds will be conducted during mowing services and all site areas, walkways, and parking areas shall be kept free of debris/trash by either sweeping or blowing and disposed of. Mowing of installation perimeter fencing shall be IAW PWS 6 2.8.1.2.

    - Improved Areas. These areas are the developed areas of the installation and will require an intensive level of maintenance. The work performed in these areas by the Contractor shall include mowing grass, edging and trimming grass, removing grass trimmings from paved areas, servicing landscaped beds, irrigating as necessary, applying fertilizer/weed control product or herbicide to lawn or landscape areas in accordance with hazards/toxics minimization and integrated pest management (IPM) requirements, servicing plants, shrubs, and flowers, performing seasonal planting of plants and flowers, removing leaves and debris, removing/applying mulch, pruning trees, removing grass from cracks in sidewalks, curbs/gutters and paved surfaces. Grass shall be cut to a height no higher than “4” and no less than “3” inches.

    - Semi-Improved Areas. Semi-Improved areas will generally be areas of the installation used for operational and maintenance purposes. The purpose of the grounds maintenance of the semi-improved areas will be predominantly erosion control, dust control, bird control in accordance with IPM requirements, the Migratory Bird Treaty Act and other applicable laws, and in coordination with DPW Fish and Wildlife Program, and clear visibility. This will include grassed areas, vegetated areas, trees, and paved surfaces. Contractor work performed in these areas shall include mowing or cutting grass/vegetation, trimming, tree pruning or tree removal coordinated with DPW Forestry Program. Grass shall be cut to a height no higher than ten (10) inches and no less than six (6) inches.

    - Unimproved Areas. Unimproved areas are acreage on which periodic recurring maintenance is performed. Activities include mowing for life, health, safety, security, weed and brush control in accordance with IPM and hazards/toxics minimization requirements, erosion control, dust control, and drainage maintenance. These areas may include but are not limited to perimeter fences, antenna fields, airfield shoulders, clear zones, drop zones and ranges. Grass shall be cut to a height no higher than ten (10) inches and no less than six (6) inches.

    - Magazine Areas. Magazine areas include non-tenant and active magazines located within the Main Plant and New River Unit. Mowing and vegetation control for each magazine shall be maintained by the regulations that govern its usage.

  - Snow and Ice Removal.  The Contractor shall perform Snow and Ice removal IAW requirements of AR 420-1, Army Facilities Management, (paragraph 7-14 and 7-18). Snow and Ice priorities map shall be provided for Government approval annually, as part of the Grounds Maintenance Plan (CDRL A07-07)

  - Natural Gas Appliance and Equipment.  The Contractor shall inspect natural gas appliance connections for leaks at the valve or adjustable meter.  The Contractor shall repair leaks immediately and conduct inspections semi-annually.  Inspections will be provided to the KO/COR within (30) days of inspection completion as part of (CDRL A07-10).  PM for natural gas appliances and equipment shall be performed IAW the requirements set forth in National Fire Protection Association (NFPA) 54 National Fuel Gas Code and 49 CFR 192, Transportation of Natural and Other Gas by Pipeline: Minimum Federal Safety Standards.  The Contractor shall maintain gas lines, gas meters, and regulators (low pressure side to include building plumbing).  The Natural Gas Distribution System includes natural gas lines outside the footprint of a building or structure up to the point of demarcation. The Points of Demarcation to the commercial source of each utility is delineated IAW PWS 10, Energy and Utilities Services. If no point of demarcation exists, then the point of demarcation is at a distance of five (5) feet out from the building. The Contractor shall remove all debris and vegetation that has grown or accumulated in Contractor-controlled areas up to the primary utility demarcation point. Cleaning shall include, but is not limited to, the removal of sand, gravel, rocks, debris, trash, roots, sod, weeds, grass trapped within the lines, manhole chambers, culverts, and curb catch basins.

  - Heating, Ventilation, and Air Conditioning (HVAC).  The Contractor shall update the PM tasks lists in Computerized Maintenance Management System (CMMS) upon installation of new equipment or removal of equipment and provide the Government with an updated task list as part of (CDRL A07-01). Services include maintenance, repair, and installation of all components, devices, and equipment. Components include, but are not limited to: boilers, furnaces, compressors, blowers, motors, drive assemblies, control systems and wiring, freeze protection sensors, duct work, burner assemblies, temperature controls, registers, condensate and drip pans and drains, grills, evaporators, air filters, and heat/air conditioning units, ensure sequence of operations is working as designed. The Contractor shall test Emergency HVAC shut off button as part of the annual Preventive Maintenance Program to ensure proper operation and verify if HVAC units tied to the shut off button are shutting off properly and resetting to normal operation. Emergency Shut-off button Testing and Preventive Maintenance will be part of PM task list. Verify if proper signage for shut off switch is provided, replace if signage is failing. Work shall conform to the technical criteria in CMMS.

    - General.  The Contractor shall operate, maintain, repair, and replace ventilation equipment and systems for comfort and non-comfort cooling requirements IAW ASHRAE handbooks, ASHRAE Standards, SMACNA duct construction Standards, and ASPE data books. Personnel shall employ Root Cause Analysis methods of problem solving and deliver workable options to the ACO/PCO/COR for consideration when work is beyond Work Order.  HVAC systems for process conditioning is included, such as exhaust fans (including bathroom exhaust systems) elevator mechanical room HVAC equipment, paint booths, welding hoods, vehicle exhaust venting systems, cold storage systems, etc.

      - Work Area/System Description. Systems and equipment covered under this Section include, but not limited to, systems and equipment such as:

- Air Curtains

- Air Dryers

- Cold Storage Plant (walk-in and reach-in)

- Kitchen Exhaust Hood and MAU’s located in DFACs

- Filters (air and coolant)

- Guards, casing, hangers, supports, platforms, and mounting belts

- Bathroom-exhaust fans

- Paint spray/vehicle exhaust equipment

- Vacuum equipment

- Domestic Hot water heaters

- Sump pumps in mechanical rooms

- Diffusers, grills, registers and pipe insulation

- Comfort Heating and Cooling

- Flue vents

- Smart electric meters, pulse kits for water and gas metering associated with Enterprise Energy Data Reporting System (EEDRS)

      - Work Performance. All work shall be performed with a minimum of disruption of occupants and disturbance of other equipment that may be in the same area. Equipment removals shall be done with care and with the intent of reusing the existing ductwork, electrical connections, vents, and other tie-ins so that the costs for re-establishing functional operations are minimized. Reuse of tie-ins for flue vents, water piping, electrical connections, ductwork, etc., shall be made to facilitate the adaptation of existing hardware and conditions to the new piece of equipment. For example, the Contractor shall supply an extension of an electrical conduit for power if the adaptation to connect the new equipment requires it for proper and safe operation. Under no circumstances shall the Contractor leave the condition of the mechanical equipment in an inferior state of repair or code compliance status due to adaptation problems, unforeseen conditions, or difficulties encountered by the Contractor. Adaptation shall include compliance with current building codes and AR 420-1.

      - Mission Essential Assets outlined in CDRL A07-04, the Contractor shall respond to repairs as Priority 1. If the repairs cannot be completed in same day the Contractor shall analyze the occupancy, use of facility and ambient temperature and provide temporary heating, cooling and/or ventilation equipment when needed or typically when the temperature in the building cannot be maintained at plus or minus five (+/-5) degrees of the established set-point. Contractor shall provide the COR and HQ, JMC hourly updates on the status of HVAC failures for critical buildings until temporary cooling/heating has been provided or the HVAC system is operational again.

    - Seasonal Changeover Requirements.

      - Schedule. Schedule and procedures will be made in accordance with AR 420-1, paragraph 23-36.

      - Spring Changeover. Spring startup/shut-down shall be accomplished during the last two (2) weeks of May, and will address the start-up of cooling systems that provide summer cooling only and the shut-down of heating systems that provide winter heating only. Seasonal weather variations may require the startup/shutdown to take placer earlier or later in the season.

      - Fall Changeover. Fall shut-down/startup shall be accomplished during the last two (2) weeks of September, and will address the shut-down of cooling systems that provide summer cooling only and the start-up of heating systems that provide winter heating only.

      - Boiler Operators will activate valves to fully discharge steam heat to occupied facilities and family housing when the outside daily low temperature falls to 55 degrees F.  If boiler operators feel that a “tickle” release of steam is required in order to warm the pipes and avoid damage prior to “full” release, then this will be accomplished when the outside temperature falls to 60 degrees F.

      - The operating contractor will keep the steam heating boilers at building 13 “idling” or in “stand-by” mode.

      - Individuals are prohibited from operating portable heating devices where the intent is to circumvent the heating standards.

    - Chemical Treatment.  The Contractor shall implement a program of chemical treatment for open and closed systems (boilers, chillers and cooling towers) specifically designed to protect the equipment, to maintain efficiencies, to conserve water and to meet State and Federal Regulations. The Contractor shall perform weekly testing for cooling tower water and add chemicals as needed. The Contractor shall maintain files of inspections and chemical usage for cooling towers, condensate and chilled water systems including laboratory analysis of all HVAC systems receiving chemical treatment. Records shall include building number, date chemicals were applied, description of chemicals used, quantity of chemicals used per system to maintain standards, chemical level readings in system before and after minor adjustments, date of inspection check and adjustment, results of inspection and name of persons doing the inspections and adjustments. All records shall be provided to the COR monthly (CDRL A07-07).

    - Related Components and Accessories.

      - The Contractor shall be responsible for all related items of equipment not previously described or identified but that are connected-to and an integral working part of HVAC systems. The Contractor shall repair and maintenance electric motors (Repair or Replacement of motor or pumps shall be high efficiency Energy Star Equipment), pumps, shaft couplings, variable-frequency-drives, drive pulleys, drive belts and belt safety- covers. The Contractor shall provide maintenance and repairs to, ladders, stairs, platforms and towers that support HVAC mechanical equipment as well as catwalks or hand railing attached to the HVAC platforms or towers.

      - Equipment/Accessories inside of Ductwork.  The Contractor shall provide maintenance and repair to HVAC system equipment installed inside ductwork such as balancing dampers, motorized dampers, control sensors, re-heat systems, unit heaters, supply fans, return fans, exhaust fans, fire alarm system duct detectors, fire system dampers-shutters-fusible links, air leaks in duct-work (loose clean-out doors, warped surfaces, broken joints, holes worn in elbows or other parts, and poor connections leading from or returning to fans, including flexible connections), duct hangers and supports

  - Roof Maintenance.  The Contractor is responsible for inspection, maintenance, and repair or roofing systems.

    - Inspection.  Roofing systems will be inspected by a qualified individual for structural adequacy and serviceability every 5 years, except:

      - Steep Roofing systems will be inspected every 7 years

      - Long Span timber trusses, heavy timber framing, masonry unit pilasters, or columns supporting structural frames will be inspected every two years

      - Timber frame buildings with high occupancy, such as theater, chapels, gyms, and assembly halls, will be inspected annually.

      - Roofing systems will be inspected after a storm or phenomena of nature that may have damaged the roofing system and after the installation of any roof mounted equipment

      - Membrane roofing systems (built-up and single-ply) will be inspected annually.

  - Roof Gutters, Drains, and Downspouts.  The Contractor shall semi-annually inspect and clean all roof gutters, drains, and downspouts. Cleaning shall include removal of bird nests, cobwebs, beehives, wasp nests, vegetation, leaves, debris, and all other obstructions that restrict flow to and through roof gutters, drains, and downspouts.  The Contractor shall replace loose, displaced, broken, or missing strainers.  The Contractor shall re-secure and fasten all loose gutters and downspouts in conjunction with inspection and cleaning.  The Contractor shall maintain a log and have it available upon request.

  - Automatic Doors.  The Contractor shall inspect and perform repairs monthly to the automatic doors..  The service includes inspecting and adjusting to confirm that all screws are tight, springs are in good shape, threshold is secure and fits properly, the on and off switch works properly, and door closing speed is adjusted to comply with the Uniform Federal Accessibility Standard (UFAS), and the Americans with Disability Act Accessibility Guidelines (ADAAG).  The Contractor shall document repairs and inspection results and make this information available upon request.

  - Overhead and Personnel Doors.  The Contractor shall annually, per schedule in CDRL A07-01, inspect and maintain the overhead and personnel doors, including electronically driven or motorized doors, operators, and controls.  The Contractor shall verify doors in fire-rated walls meet the corresponding fire rating required by the building code(s).  PM shall include inspection, adjustment, alignment, proper fit, testing of controls and safety devices, and lubrication of overhead doors.

  - Gates, Fences, Barriers and Dock Levelers.  The Contractor shall be responsible for the maintenance and repair of gates, fences, (to include rock or Concrete Mason Unit [CMU] privacy or security walls), and barriers. Barriers include but not limited to guardrails, bollards, bumper blocks, parking lot wheel stops, and similar items. Automatic or motorized opening/closing devices and their associated controls are included. Locks and latches that are part of the gate (i.e., not a chain and padlock) are included. The installation and removal of fence screening materials is included. Signage on gates, fences, and barriers required by physical security regulations shall also be maintained and replaced as needed. Contractor shall replace faded and/or damaged signage on perimeter fencing. The Contractor shall keep all fencing material and barbed wire free of trash. Additionally, the Contractor shall perform maintenance, repair, and modification as required on all types of wire and cable fencing and gates, to include but not limited to, security and non-security chain link fences, barbed wire posts and gates, and various steel gates. Chains and protective wire barriers around improvements or hazardous areas shall be maintained. Gates with automatic or motorized opening/closing devices shall be inspected and serviced, but in no case less than annually. Gates with serviceable equipment such as wheels or guides shall be serviced annually. The Contractor shall accomplish installation of new fence as required. Fencing of secure areas shall be maintained to the requirements of AR 190-13, The Army Physical Security Program, and AR 190-51, Security of Unclassified Army Property (Sensitive and Non-sensitive), and requirements in the Security PWS. The Contractor shall maintain a twelve (12) foot dirt road adjacent to perimeter fences within RFAAP property free of all vegetation and fence holes (e.g., coyote hole).

  - Air Compressors/Unfired Pressure Vessels.  The Contractor shall inspect, maintain, and test the air compressors/unfired pressure vessels annually and have the results available upon request.  The Contractor shall develop a Preventive Maintenance plan for the air compressor systems including air receiver, air drier and associated piping (CDRL A07-01). The PM plan shall include frequencies of inspections and be in accordance with original manufactures recommendations. The Contractor shall complete and provide to the KO/COR monthly maintenance reports as part of the (CDRL A07-07).

    - Refrigerated Air Dryer.   The Contractor shall inspect refrigerated air dryers, if present, for proper operation and create a Work Order for non-routine maintenance repairs.

    - Compressor Storage Tanks.  The Contractor shall not perform welding of ASME certified storage tanks.   If an air storage tank is suspected of having a problem, the KO/COR shall be notified within twenty-four (24) hours.  The Contractor shall inspect the compressed air distribution piping annually and ensure no leaks are present. The Contractor shall document repairs and inspection results and make this information available upon request.

  - Plumbing.  Plumbing includes potable water systems consisting of hot and cold water piping, components inside the facility, and out from the facility to the point of demarcation.  Waste, vent, and drain systems consist of piping and components inside the facility and out from the building to the point of demarcation.  Potable water system includes domestic water heaters.  Water heater types may be electric or fueled by natural gas, oil, or gas/oil combination with either atmospheric or forced draft burners.  The Contractor shall repair, replace, and maintain potable water and waste, vent, and drain systems and components from the isolation valve. All work shall be completed IAW AWWA and UFC 3-420-01.

    - Components. Components include, but are not limited to, the following: hot and cold water piping and fittings, insulation, natural gas piping systems downstream of the meter owned by the utility provider, sinks, faucets, hot water storage tanks, eye wash stations, drinking fountains, hot water circulation pumps, hose bibs, standpipes, expansion tanks, relief valves, mixing valves, flushometers, bathtubs, commodes,  piping, fittings, drains, sump pumps, motors, and sump water level controls IAW Army Regulation (AR) 420-1, Army Facilities Management.  The Contractor shall set hot water temperature IAW AR 420-1.

    - Leaks.  The Contractor shall repair leaks of piping and plumbing fixtures.  System and components in mechanical rooms shall function properly in the event of water leaking from valve and pump packings or seals.  Sewage gases shall not be vented into facilities.  Drains shall be free of obstruction.  Fuel oil or natural gas shall not leak from the system or components.  Hot and cold water shall flow on demand through the piping systems with no leakage through closed faucets, mixing valves, or flushometers.  Flushometers shall operate properly and shut off the water flow after the flush cycle.

      - Gas Leaks.  The Contractor shall repair all gas leaks from the storage tank to the inside of the buildings.  When repairing gas leaks the Contractor shall test the entire building system for leaks and repair all as needed.  Gas service to the building will not be restored until leak tests pass for the entire building system, not just the section that was replaced or repaired.   All tests and repairs shall be IAW applicable industry codes.

    - Sump Pumps and Septic Tanks.  The Contractor shall annually inspect, remove all debris, wash down, and operate the sump pumps and lift stations. Sump tanks shall not exceed their maximum capacity.  Sump water level controls shall energize the sump pump prior to the sump becoming full and shut off the pump after sump draining is complete.

    - Water Heaters.  The Contractor shall inspect water heaters per schedule in (CDRL A07-01).  Inspection shall include a visual check for leaks, corroded surfaces, and improper setting of aquastat.   PM shall include checking operation and condition of relief valve, draining of water heaters, and ensuring that there is an unobstructed flow through the exhaust line for gas water heaters.  Water heaters Hot Water Tanks with forced draft burners shall perform in compliance with the Air Operating Permit, American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code.  Burner combustion exhaust emissions shall not exceed fifty (50) parts per million (ppm) of carbon monoxide when burning liquid propane gas, or a No. 1 (20% density) smoke on the Ringlemann Chart.  Work shall be scheduled and performed with minimum impact to the facility mission.

    - Backflow Preventers. The Contractor shall develop and submit, for approval by the KO, a PM Program to annually inspect, certify, and repair all backflow prevention devices.  Work shall meet the requirements of the applicable Safe Drinking Water Act (SDWA), AWWA standards, and RFAAP backflow program.

    - Restroom Fixtures.  The Contractor shall repair and replace all restroom fixtures including but not limited to sinks, toilets, mirrors, urinals, partitions, doors etc as required.  Clogged drains and odor complaints shall be performed through a CMO.

    - Wash Facilities/Racks.  The Contractor shall provide maintenance and repair to keep wash facilities properly operational.  This includes vehicle wash points, vehicle wash facilities, tracked vehicle washers, and the trash container/dumpster wash point.  Additional components including, but are not limited to, wash stations, valves, sediment basins, oil skimmers, sensors, sand traps, drains, lines, detention ponds, wash water, concrete and filter pumps, oil-water separators, make-up water systems, motors, gearboxes, piping, electrical systems.  The Contractor shall provide regularly scheduled and unscheduled repairs.

      - Confined Space Entry. When Confined Space Entry, as defined by OSHA is required to clean the oil/water separator, a Confined Space Entry plan and access permit, shall be obtained from the RFAAP Safety Division at least three (3) business days in advance of this work. The Contractor shall provide all personnel training and personal safety equipment, including appropriate breathing apparatus, if required at no additional cost to the Government. The Contractor shall not start work until the plan is approved. (Reference Safety PWS for additional guidance)

  - Industrial Wastewater Treatment Plant (IWTP).  Due to the variation in flow and the large amounts of suspended solids in the industrial wastewater, equalization basins are provided at the treatment plant site for settling, solids, flow equalization, storm water storage, and oil removal.  Aerated biological ponds are provided at the IWTP site to remove Biochemical Oxygen Demand (BOD) prior to discharge to the STP.  Rags, suspended solids and oil are removed prior to discharge to the equalization basins, under dry weather conditions.

    - Components.  IWTP equipment and components include, but are not limited to: mechanical bar screens and grit collection system, recirculating systems, chemical storage and pumping systems, channel and gate bypass systems, pumping and distribution systems, electrical and digital control systems, alarm systems, valves, piping and fittings, controllers, and regulators.  IWTP repairs include, but are not limited to: removing visible corrosion, rust, fatigue, breaks, leaks, blockages, unusual noise, vibration, temperatures, levels, and hazardous conditions.  The IWTP is subject to compliance inspections at any time without prior notification.

    - Compliance.  The Contractor shall maintain, repair, and replace IWTP systems and components, and TM 5-814-3 Domestic Wastewater Treatment Plant Laboratory Guidance.  The Contractor shall notify the COR of system bypasses and again after system is returned to normal operation.

    - Reporting Requirements.  The Contractor shall submit a maintenance plan for the IWTP work as part of (CDRL A07-01).

  - Heating/Cooling Plants.  The Contractor shall inspect, maintain, repair, and service all heating plants and systems (steam meters and automatic tank monitoring system), all boilers, and furnaces used in the production of domestic heat.

    - Maintenance of Heating Plants.  PM shall be planned, scheduled, and conducted.  Gas and oil-fired boilers shall receive PM prior to the onset of the heating season.

      - The Contractor shall inspect, maintain, and repair all heating plants and associated equipment. M&R of high pressure boilers shall be performed IAW UFC 3-430-07.  IF outside subcontractor is required it will be at the operating contractor’s expense.  The results of these Inspections, along with records of repairs shall be recorded and maintained; copies of the inspection reports and records of all repair performed throughout the year shall be provided to the ACO/PCO no later than 30 November of each year (CDRL A07-10).   M&R of central boiler plants shall include steam and hot water heating sources, fuel storage, and handling equipment at the boiler plants, feed water, condensing flue gas and air system equipment, miscellaneous pumps and plant instrumentation.  M&R performed by the Contractor shall be accomplished so equipment condition will remain unchanged from the time of receipt.

    - Scheduled Systems Outages.  The Contractor shall coordinate all scheduled outages with the COR.  Outages shall be coordinated at least fourteen (14) working days in advance.  The Contractor shall notify affected Installation Agencies of the scheduled outage.  The Contractor shall attend, as applicable, planning meetings that may affect the air conditioning systems the Contractor operates and maintains.  The COR will notify the Contractor at least forty-eight (48) hours in advance of planned meetings.

    - Perform Seasonal Start-up and Shutdown of AC Plants and Systems.  The Contractor shall perform the seasonal start-up and shutdown of the AC plants and systems within five (5) days of notification by the COR.  Seasonal shutdowns shall include winterization of condensers and shutoff for each system and item of equipment, including draining of lines, coils, and tanks and application of freeze protection where required.

    - Freeze Protection.  The Contractor shall shut down, secure, and drain all equipment subject to freeze damage when freezing weather conditions are forecast, anticipated, or imminent.  The Contractor is responsible for and liable to provide such services whether or not specifically informed or notified by the COR, of such conditions.  All equipment secured and drained for these reasons shall be returned to normal service when danger of freeze conditions has passed.  The Contractor shall be liable for correction of any and all damages incurred as a result of failure to adequately protect equipment under these conditions.

  - Winterization and De-Winterization (Mothballed Buildings).  The Contractor shall winterize and de-winterize the non-heated facilities, other non-heated systems, and wood heated facilities as necessary. The Contractor shall be responsible for identifying and correcting any deficiencies that present a potential for freeze damage or water leak damage.

    - Winterization and de- winterization shall include, but not be limited to: preventing freeze damages, removing parts/reassembling removed parts and equipment of building plumbing, electrical and other equipment; turning off/turning on utilities including, but not limited to, electricity and water; adding/draining antifreeze from mechanical systems; checking mechanical systems including, but not limited to, the plumbing system, heating system, and building equipment for proper operation; repairing leaks and malfunctions due to freeze related damages; and turning water off/on at underground shutoff valves. Contractor shall adjust the vacant building requirements as needed to address special situations such as facilities under renovation, facilities partially occupied, vacant, etc.

    - Identify different levels of mothballing - short term, long term, and demolition. The Contractor shall develop and maintain a Vacant Facility Maintenance Program that is approved by ACO/PCO, the Contractor shall sign for vacant facilities from the Real Property Office, perform scheduled inspections of vacant facilities and shall correct observed deficiencies. The Contractor shall address all life, health and safety issues identified during walkthroughs and make repairs. The program shall at a minimum address the three (3) categories of vacant facilities as follows:

- Short term vacancies – Unoccupied periods less than ninety (90) calendar days: Contractor shall ensure facilities are secured including but limited to broken window repair and closing/locking open doors/windows, maintain fire detection and suppression, maintain unoccupied temperature set points IAW AR 420-1, Army Facilities Management maintain plumbing trap levels, and pest control. Utilities shall not be shut off for short-term vacancies. Contractor shall conduct walkthrough of facility on a weekly basis and shall include repairing of deficient components. CMO or work order repairs and renovations may occur during this period. The Contractor shall provide a monthly report of short-term vacant buildings inspected to the COR.

- Long term vacancies – Unoccupied periods greater than ninety (90) calendar days: Contractor shall ensure facilities are secured including but limited to broken window repair and closing/locking open doors/windows; fire detection; maintain unoccupied temperature set points IAW AR 420-1, Army Facilities Management; maintain plumbing trap levels; and pest control. Utilities shall be shut off for long term vacancies except as needed to prevent freezing of water lines, provide security lighting, fire detection, intrusion detection (if facility is equipped).

  - Contractor shall conduct walkthrough of facility every two (2) weeks, and validate HVAC set points to ensure proper settings or prevent tampering by other parties. DMO or work order repairs and renovations shall be completed prior to winterizing the facility.

  - The Contractor shall provide a report of long-term vacant buildings inspected to the KO/COR.

- Vacancies in preparation for demolition - Unoccupied, with no plans for future use. Contractor shall turn off all utilities except as needed to prevent freezing of water lines, fire detection and fire alarm panel operation, and security lighting. The Contractor shall ensure facilities are secured including but limited to broken window repair and closing/locking open doors/windows. Contractor shall conduct walkthrough of facility on a monthly basis and validate HVAC set points to ensure proper settings or prevent tampering by other parties. Pest control shall be provided via OWO when needed.

- Contractor walkthroughs – The Contractor shall inspect the facility for damage, debris, pest infestations, vandalism, mold, etc. Contractor shall verify proper operation of systems that are still operational (fire alarms, P-traps, security lighting, etc.). Contractor shall initiate DMOs to address any issues discovered during the walkthroughs to only include life, health and safety. Documentation of the walkthrough inspections shall be submitted to the KO/COR.

- Documentation of the walkthrough inspections shall be submitted to the KO/COR. Historic Real Property may require additional reporting on a case-by-case basis and shall have all proposed work comply with the National Historic Preservation Act, Section 106 (http://www.achp.gov/work106.html) and the Secretary of Interior Standards of Treatment of Historic Properties (https://www.nps.gov/tps/standards.htm).

    - Specific tasks related to systems.

  - Fire Suppression Systems

    - Short term – None. Fire suppression systems shall remain active

    - Long term – None. Fire suppression systems shall remain active

    - Long term – None. Fire suppression systems shall remain active

  - Gas Systems

    - Short term – None

    - Long term – All gas fire appliances except those needed to maintain HVAC unoccupied set points shall be turned off

    - Demolition – Same as long term

  - Electric Systems

    - Short term – All circuits shall remain on. Facility shall be inspected and any unnecessary equipment that is plugged in shall be unplugged

    - Long term – All circuits shall remain on. Facility shall be inspected and any unnecessary equipment that is plugged in shall be unplugged

    - Demolition – All circuits shall be turned off except those required for the fire alarm and suppression systems and security lighting

  - Fire Alarms

    - Short term – None. All fire alarm and detection equipment shall remain active

    - Long term – None. All fire alarm and detection equipment shall remain active

    - Demolition – None. All fire alarm and detection equipment shall remain active

  - HVAC

    - Short term – HVAC equipment shall be set to unoccupied set points. Routine scheduled maintenance shall continue during the unoccupied period

    - Long term – HVAC equipment shall be set to unoccupied set points. Routine scheduled maintenance shall continue during the unoccupied period

    - Demolition – All HVAC equipment shall be turned off. Outside air dampers shall be placed in the closed position

  - Plumbing

    - Short term – all plumbing shall remain on. Traps shall be maintained and not allowed to dry out

    - Long term – domestic water shall be turned off (fire suppression water supplies will remain active). Traps shall be treated to prevent drying out and periodically check and refilled if needed. Backflow prevention devices shall continue to be tested and maintained; temporarily turning on water to the facility if required for testing of the device

    - Demolition – same as long term

  - Timeline to bring buildings back online

    - Short term – Fifteen (15) calendar days – Contractor turn on all systems as needed to bring the facility back into date the facility is due to be re-occupied

    - Demolition – Sixty (60) operations. Contractor shall flush all water lines. Contractor shall complete all outstanding OWOs by the date the facility is due to be re-occupied

    - Long term – Forty-five (45) calendar Days – Contractor turn on all systems as needed to bring the facility back into operations. Contractor shall flush all water lines. Contractor shall complete all outstanding OWOs by the calendar days – Contractor shall prepare a proposal for all work required to bring the facility back into use

  - Lift Stations.  The Contractor shall evaluate lift stations, collect and record data, perform adjustments necessary to control the quality of the operations, inspect for deficiencies and hazardous conditions to determine the plant M&R requirements.  Perform routine cleaning of equipment subject to waste material accumulations, blockages, algae growth, vector attraction, and offensive odors including, but not limited to, bar screens, grit collector, de-gritter, and weirs.  Dispose of grit, scum, and screening material removed from the facility waste streams.

  - Sedimentation Tanks Maintenance.  The Contractor shall perform maintenance cycles IAW checklists in the maintenance plan.  The Contractor shall clean each sedimentation tank semi-annually.  The Contractor shall be responsible for the cleaning, pumping, and unplugging of motor pool oil separators.  The Contractor shall maintain the entire collection system in a free flowing condition at all times.  The Contractor shall notify the COR within one (1) hour of notification of plugged sand traps and interceptors.

  - Electrical.  The Contractor shall perform scheduled inspection, testing, calibration, maintenance, repair, and other services of electrical systems and components.

    - Emergency Fixtures.  The Contractor shall inspect, test, repair, and maintain lighted exit signs and emergency lighting units located within building interiors. Inspection and testing shall be part of the scheduled inspections under Section 2.22 below.

  - Auxiliary Generators. The Contractor shall perform repair and maintenance on all generators and associated transfer switches at RFAAP. Monthly and annual checklists might change due to change in regulations. Inspector must notify COR/KO within twenty-four (24) or earlier when a deficiency is observed. (for Air permitting requirements reference Environmental PWS)

    - Perform PM of Auxiliary Generators. The Contractor shall perform PM of the auxiliary generators listed IAW TM 5-682, TM 5-683, TM 5-684, TM 5-811-3, and the PM checklists.  The Contractor shall follow the special schedule requirements specified in AR 420-1, Army Facilities Management Section 4-67 and 23-54.  The Contractor shall coordinate all electrical testing of generators and applicable activities with the COR prior to testing. All lubricants, filters, belts, fittings, indicator light bulbs, and fasteners are to be provided by the Contractor as part of the PM requirement.  Repair requirements above and beyond the scope of auxiliary generator PM shall be submitted to the COR within twenty-four (24) hours of identification.  The Contractor shall prepare and implement a PM plan for Emergency Generators and transfer switches and submit for approval to the KO/COR within fifteen (15) calendar days of the start of the contract as part of (CDRL A07-01).  At a minimum, the PM plan shall report condition of critical engine components, Automatic Transfer Switch (ATS) and report ability of ATS to operate normally. The Contractor shall run the generators twice a year for a minimum of one (1) hour loaded, and twice a year for a minimum of one (1) hour unloaded. The Contractor shall inspect the associated equipment and components that are necessary for the proper operation of the generator (e.g., batteries, switchgear, fuel tanks, belts, and coolant). Inspections must be conducted monthly and reported to COR/KO by the end of each month (CDRL A07-0z).  The Contractor shall inspect the fuel levels of emergency generators and refuel to optimal fuel.

      - Temporary Generator. The Contractor shall provide temporary generator support. In the event of loss of power of Mission Essential Assets (CDLR A07-04) the Contractor shall provide temporary power to prevent mission impact upon request by COR.

  - Grounding Points, Lightning Protection, and Cathodic Protection Maintenance

    - General.  Contractor shall maintain and repair all grounding and lightning protection systems protect facilities, personnel, and   equipment IAW UFC 3-575-01.  These are located at ammunition supply and handling facilities at RFAAP.

    - Grounding Point Checks. The Contractor shall perform grounding point testing on all points, metal bleacher covers, and facilities on an annual basis IAW the latest edition of the National Fire Protection Association (NFPA) standards for the installation of lighting protection systems.  See Grounding Points, Lightning Protection and Cathodic Protection. See MTE0016, List of Facilities with Lightning, Grounding, and Cathodic Protection Systems for type of grounding systems, frequency of testing, allowable resistance levels, and locations. The Contractor shall check the grounding points in all buildings (e.g., ammunition storage, supply points, airfields, helipads/heliports) as required. The Contractor shall inspect and test grounding systems protection per NFPA 70, NFPA 780 and PAM 385-64 Standards. All deficiencies shall be corrected IAW NFPA 70, NFPA 780 and PAM 385-64 Standards.

    - Grounding Protection System (GPS).  A grounding protection system is designed to protect personnel and equipment from injury or damage due to unwanted voltage differences by providing a very low impedance path to ground. A grounding protection system includes a network of air terminals, bonding conductors, and ground electrodes designed to provide a low impedance path to ground for potential voltage sources.

    - Lightning Protection System (LPS).  Lightning protection systems are used to prevent or lessen damage to structures done by lightning strikes. Lightning protection systems mitigate the fire hazard, which lightning strikes pose to structures. A lightning protection system provides a low-impedance path for the lightning current to lessen the heating effect of current flowing through flammable structural materials.

    - Cathodic Protection System (CPS). Cathodic protection is designed to reduce corrosion or transfer the corrosion to another location of the system. The Contractor shall maintain and inspect cathodic protection systems. Cathodic protection systems protect metal structures such as water storage tanks and underground utility piping from corrosion.

    - Visual Inspections shall be conducted Yearly.  The Contractor shall test and certify the GPS, LPS and CPS every year as required by NFPA and shall provide test and inspection results to the COR and the Installation Safety Office (CDRL A07-10).

  - Fire Alarm, Fire Suppression and building Mass Notification Systems.

    - Fire Alarm Systems.  The Contractor shall conduct routine inspection, testing, and maintenance of D-21 monitoring systems, fire detection and fire suppression and building mass notification systems IAW the latest edition NFPA 72, National Fire Alarm and Signaling Code and UFC 4-021-01 where applicable. Fire suppression systems are sprinkler systems (wet pipe, glycol, dry pipe, dry chemical, wet chemical, INERGEN and AFFF), kitchen hoods and grease laden exhaust systems. Completed inspection testing and maintenance forms shall be provided to the Fire Inspector and made available upon request for the life of the contract.

      - Preventive Maintenance Requirements

        - The Contractor shall develop and submit to the KO/COR and the Fire Department a schedule of the services within fifteen (15) calendar of the start of the contract. The Contractor shall update the schedule annually (CDRL A07-01).

        - The Contractor shall conduct inspection, testing, and maintenance of kitchen fire detection and suppression systems, including gas and electrical safety shut off devices.

        - The Contractor shall inspect and test all types of fire suppression systems (wet pipe, glycol, dry pipe, dry chemical, wet chemical, and AFFF), Facility fire alarm systems and associated communication devices as required by applicable NFPA 25.

        - The Contractor shall conduct acceptance testing of new or existing fire alarm systems, and fire suppression systems.

        - The Contractor shall maintain Building Mass Notification Systems (MNS) internal to the buildings and associated components IAW applicable codes and standards and as required.

    - Sprinkler and Hood Suppression Systems.  The Contractor shall perform PM services on sprinkler systems and components listed IAW the latest edition of NFPA 25, Standard for Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems and on hood suppression systems IAW the latest edition NFPA 17, Standard for Dry Chemical Extinguishing Systems for dry chemical systems and NFPA 17A, Standard for Wet Chemical Extinguishing Systems for wet fire extinguishing systems. The Contractor shall coordinate with the fire department and perform inspection, maintenance, and testing of fire protection systems. The fire protection systems shall comply with applicable NFPA Codes and TM 5- 695, Maintenance of Fire Protection Systems.

    - Notify RFAAP Fire and Emergency Services prior to taking facility fire suppression systems out of service, and within one (1) hour after system is restored to service.  If the system is out of service for more than four (4) continuous hours in a twenty-four (24) hour period, notify the COR and Facility Manager to provide a fire watch or evacuate the facility until the system is returned to service. Maintain records by building of each system. Document all work performed to the respective system in the record.  These records shall be made available for review by the Government when requested.

  - Elevator Maintenance.  The Contractor shall inspect, test, repair and maintain elevators and escalator at the facilities on RFAAP. The Contractor shall coordinate directly with the facility users for scheduling of all work and access to the buildings and elevators. The COR shall assist only when the Contractor cannot gain reasonable access.

  - Elevator Inspection and Certification.  Inspection and testing shall be performed with a Contractor-provided Certified Inspector. Inspection and testing shall be IAW the following:

      - Local requirements

      - ASME A17.1, A17.2, A17.3,

      - NFPA standards

      - National Electrical Codes (NEC)

      - Nevada 455 C

      - Certificate of Elevator Inspection GSA Form 55 and Acknowledgment of Elevator Inspection Certificate GSA Form 55A or a form approved by KO/COR

    - The Contractor shall obtain an Annual Elevator certificate of operation. The Contractor shall post a notice inside each elevator noting the date of the completed annual certification and note that certificates are on file and available upon request. The Contractor shall create a schedule of inspection, testing, maintenance, repair and certification within thirty (30) days of the contract start date and submit to the KO/COR for approval annually (CDRL A07-01). The Contractor shall coordinate any scheduled shutdown with the affected building occupants after written approval is provided by the KO/COR. In the event that an unscheduled shutdown of an elevator occurs, the Contractor shall notify the KO/COR within two (2) hours.

    - Out of Service Time.  Elevators shall not be out of service for more than twenty-four (24) hours at any one time without approval from KO/COR. When parts are ordered, the KO/COR will be notified on the status and due delivery date. If the Contractor knows that the elevator is going to be down more than seven (7) calendar days, the KO/COR shall be informed in writing/email detailing the specific problem and indicating why the elevator will be down for more than seven (7) days. The Contractor shall post a Status of Repairs on the elevator door indicating the “repair by” date.

    - Preventive Maintenance Requirements and Scheduled maintenance Requirements. Includes monthly preventative maintenance; shop parts and supplies; inspections and reports. Monthly preventative maintenance includes but is not limited to the following: lubricate equipment, adjust parts and components, re-lamp signals, and examine all elevator equipment for optimum operation. All maintenance and work shall be performed IAW OEM requirements and industry standards.

      - Periodic Inspections, Testing, and Reports. The Contractor shall perform annual inspection/testing and make a formal report IAW industry standards (CDRL A07-10). Schedule for Annual inspections shall be submitted for approval to the KO/COR within thirty (30) calendar days of the start of the contract. The Contractor shall also fill out DA Form 7485-R and submit the completed form to the KO/COR within ten (30) calendar days after completion of each Annual test (CDRL A07-10).

      - General PM Requirements. The following items shall be provided by the Contractor to support the maintenance and repair services.

  - The Contractor shall keep each logbook in the machine room of each elevator, maintain logbook to include records of scheduled maintenance services, annual service, testing, service calls, repairs and parts replaced. Information shall contain description of work, dates, problems, and corrective measures taken, persons requesting services/repairs, time completed, and the name of the mechanics performing the work. The logbook shall be hard bound. Existing logbook may be continued if the book is in good condition. Retain previous log books and records in a binder or other suitable document container. Logbooks will become Government Property.

  - Work covering routine cleaning and refinishing of the interior of cars and the exterior of hoist way doors and frames is not included in this contract. However, cleaning of equipment spaces, hoist ways, and daily cleanup of job sites in conjunction with preventative maintenance, inspection services, and repairs is included in this contract. Provide a metal waste can with cover in each elevator machine room

  - Keys and Locks.  The Contractor shall repair all door and gate locks, and provide for the replacement of keys and hardware IAW AR 190-11.  Locksmiths must possess a Tier 3, SECRET Clearance or be capable of obtaining a Tier 3, SECRET Clearance and be State-certified.  Contractor must use a Master Key System database for keys and lock interchangeable coring (IC).  There are two (2) lock systems to be used on RFAAP.   Best and Medco both use propriety keyways for Army applications. Customers submit requests for additional key duplication.  Rekeying of buildings will not occur unless directed or approved by the COR.

    - Locksmith services shall include facility locks and other lock types such as safes, arms room’s doors, Sensitive Compartmented Information Facility (SCIF), BOC, and Network Operations Center (NOC) locks, card key locks, and other type locks including controlled access, high security locks, magnetic locks, and including ancillary equipment. The Contractor shall perform all necessary tasks to install, program, operate, maintain, repair and replace and maintain electronic computer-based building access systems. The Contractor shall provide and replace system PC’s, software, supplies and other peripherals associated with these types of systems.

    - Compliance Locksmith Services to be performed to accepted professional practices and standards and must meet applicable codes.

      - Repair of locks. Contractor shall respond to broken locks as Priority 1 DMOs. Contractor shall repair broken locks (or otherwise secure the facility) by close of business.

      - Lockouts. Contractor shall respond to lockouts as Priority 1 DMOs. Contractor shall respond to barracks lockout situations by providing access to a room upon verification from Barracks Manager that the unit has made every attempt to open or unlock electronic locks.

      - Rekeying. Contractor shall perform re-keying IAW key control procedures. Providing of new keys or rekeying of locks shall be performed upon receipt of a memorandum from the key control officer of the facility.

    - Key Control in Contractor Occupied Facilities. The COR will provide the Contractor with a set of keys to areas not open and accessible.  The Contractor shall establish and implement methods to ensure keys are not used by unauthorized persons.  The Contractor shall develop procedures covering key control in the Quality Control Plan.  The Contractor shall immediately report any occurrences of lost or duplicate keys to the COR.  All references to keys include key cards.

    - Lost keys shall immediately be reported by written correspondence to the KO/COR/UH. In the event keys (other than master keys) are lost or duplicated, the Contractor shall, upon approval of the KO/COR, re-key or replace the affected lock or locks. In the event a master key is lost or duplicated, all locks and keys for that system shall be replaced at the Contractor’s expense.

      - The Contractor shall prohibit the use of Government issued keys by any persons other than the Contractor’s employees. The Contractor shall prohibit the opening of locked areas by Contractor employees to permit entrance of persons other than Contractor employees engaged in the performance of assigned work in those areas, or personnel authorized entrance by the KO/COR.

    - Lock Combinations.  The Contractor shall establish and implement methods of ensuring that all lock combinations are not revealed to unauthorized persons. The Contractor shall ensure lock combinations are changed when personnel no longer require access.

  - Food Service Equipment (FSE) This contract is responsible for food service equipment in various buildings and Fire Stations.

    - General.  The Contractor shall perform maintenance and repair of food service equipment.

      - Description of equipment: Contractor shall provide list of all Food Service Equipment. List shall include a preventive maintenance schedule for equipment (such as cleaning refrigeration coils, testing gas safety equipment, etc.).  For refrigeration and hot water systems, the preferred set point and the allowable operating temperature range shall be noted.

      - Action After Maintenance or Repair. After completion of a maintenance or repair task, the Contractor shall ensure that the equipment or area is safe, operational, and clean so that food preparation can commence without effort beyond normal by food service personnel. Contractor shall report results to the DFAC Manager and the KO/COR.

  - Crane and Load Scales Maintenance and Load Testing

    - General.  Contractor shall repair, maintain, and provide annual testing of Cranes IAW 29 CFR 1910. Crane types can be JIB, Bridge Crane, and Gantry Cranes installed within RFAAP.

    - Preventive Maintenance Plan. The Contractor shall develop, implement, and submit for approval to the KO/COR, a PM plan for crane, cable and rail, inspection and annual load testing. Inspection requirements shall be derived from information provided by the crane manufacturer and TB 43-0142 (CDRL A07-01). Inspection procedures should state the acceptance criteria for inspections and tests and shall be specific for the applicable make and model of crane.

    - Crane Operator Training.  Quarterly, the Contractor shall conduct a training session to instruct building occupants on the safe and proper use of cranes (CDRL A07-03). The Contractor shall submit a schedule and time, location, attendees w/signatures and syllabus for approval to the KO/COR within fifteen (15) calendar days of the start of the contract. Trained crane operators or technicians shall conduct the training. The Contractor shall install signage at each crane, in an appropriate and visible location, that states: “Cranes to be operated by trained personnel only. Improper use of cranes can result in injury, death, and damaged equipment. Repair costs of cranes damaged by improper use or abuse shall be paid by the unit. BASOPS Contractor conducts quarterly training on the safe and proper use of cranes. All personnel operating cranes shall attend this training. Contact contractor to attend this training. Repeated damage to cranes due to misuse shall be reported to the KO/COR”.

    - Load scales. Contractor shall perform maintenance on permanent loading scales. The permanent scales.

  - Glass, Glazing and Asbestos.

    - The Contractor shall replace all broken glass and replace with like material in response to a valid DMO.

    - Damaged glass shall be removed and replaced with a like material. If required, rotten wood including sills, sashes, muntins, and frames will be removed and repaired. Sills will be re-sloped to encourage water run-off. Mullions shall be reinstalled where required. All work shall be sealed appropriately to prevent water infiltration. The replaced portions shall be painted to match existing finish current on the windows. All removed hardware will be securely stored and cleaned or replaced upon completion. Any of the adjacent shingles on an exterior wall surround requiring removal during completion of this process shall also be replaced and repainted in-kind.

    - Upon completion of a project, the work area will be cleaned and waste materials and debris will be properly disposed of.

    - Replacement on windows on a historical building will follow guidance as specified in the Secretary of Interior Standards for the Treatment of Historic Properties and as directed by STATE HISTORIC PRESERVATION OFFICE (SHPO)

    - Any work involving lead-based paint or asbestos containing material (ACM) will be handled IAW applicable Regulations.

      - Contractor is responsible for assuring all ACM is maintained in an encapsulated or non-friable state.  All ACM found in a friable state must be re-encapsulated or abated by licensed individuals.

- Operation and Maintenance of Energy Conservation Systems.

  - General. Contactor (Contractor) shall repair and maintain Photo Voltaic Systems, the Solar Day Lighting Electrical Systems, and other Energy Conservation devices and equipment for proper operations. Maintain the operational readiness of all Solar Photovoltaic Systems (PV), Solar Day-Lighting Systems, and other Energy Conservation means (to include its components, devices and equipment), to operate twenty-four (24) hours per day / seven (7) days a week. The Contractor shall provide to the KO/COR schedules (CDRL A07-01), inspection reports (CDRL A07-10) and maintenance records (CDRL A07-07) monthly. For specific Regulations and guidance please reference the Energy and Utilities PWS.

    - Replacement of Solar Panel. Should a solar panel become unserviceable and require replacement, DPW KO/COR approval is required prior to the purchase of replacement panels. Once purchased, the replacing of a panel is defined as repair and maintenance.

    - Roof Leaks. Roof leaks associated with the Solar Day Lighting Systems are included.

    - Occupancy Sensors. Occupancy Sensors shall be used when repairing or replacing any single toggle switch controlling lighting. Energy conserving devices shall not be removed without Government approval.

    - Replacement Standard. Replacement lighting products shall be Energy Star rating. All lighting lamps and tubes acquired for replacement shall meet energy efficient standards.

  - Preventive Maintenance Requirements. The Contractor shall establish and perform all monthly and as-needed inspections and maintenance. Some minor repairs may be needed as part of this PM. This PM Schedule shall be established in GFEBS and submitted as part of the Deliverable.

    - Monthly Inspections and Maintenance PV. Photo Voltaic (PV) Systems shall include the below at a minimum.

      - Inspect inverter for damage.

      - Inspect structure and solar panels for signs of wind damage.

      - Inspect panels for damage, bending, and/or cracks.

      - Inspect panels for loose and/or dangling wires.

    - Washing of Photo Voltaic Systems. The contractor shall perform monthly washing of solar PV panels. Inspect each solar PV panel (active side/side facing the sun) for excessive dust and/or dirt. If dust and/or dirt are on the panel wash and dry the panel. Clean the Inverter cabinet.

    - Solar Day Lighting Electrical Systems. The Contractor shall inspect all operator switches. Inspect interior and exterior lamps for yellowing, darkening, fading, and murkiness. Clean and make necessary repairs.

    - Sensor Adjustment. Adjustment of occupancy sensors for electrical lighting shall be accomplished during inspections and/or repairs per energy efficient standards.

    - Efficient Upgrade. Whenever a repair or replacement is made on light fixtures, the Contractor shall discontinue and properly dispose of inefficient light bulbs/tubes and replace with a more efficient version. Replacement stock shall be updated to include the efficient replacement parts.

- Sign Shop Operations

  - General. The Contractor shall repair, install, replace, remove, design, layout, paint, stencil, fabricate and mount permanent and temporary signage throughout the Installation. Signage shall include directional, regulatory, informational, and other types of signs. Signage work shall also include, but not be limited to, designing, fabricating, and painting hard surface informational, directional, traffic, warning, and safety signs. The Contractor shall paint traffic signs in strict conformance with the standards set forth in the Manual of Uniform Traffic Control Devices for Streets and Highways, all Army, IMCOM, and USAG XX Installation Design Guide (IDG), including the Manual on Uni-form Traffic Control Devices for Streets and Highways. The Contractor shall maintain signs on buildings (excluding privatized housing), structures, appurtenances, and along streets so that they are properly positioned, clean, and legible at all times. The Contractor shall use reflective materials on all signs.

    - Sign Design. The Contractor shall design layout, draw, letter, and paint IAW specifications provided by the Customer through a valid work document. The Contractor shall reference the specifications/Standards for each sign that is installed. The Contractor shall draw in detail from rough sketches, drawings, or photographs. The Contractor shall design, fabricate, and paint or use a bonding machine for traffic signs, informational signs, directional signs, field training signs, and safety signs. The Contractor shall cut, punch, round corners, file, trim, assemble, install, and remove signs of different materials and gauges such as aluminum, galvanized sheet metal, plastic, wood, masonry, and black iron. The Contractor shall use Helvetica medium, upper and lower case, and numbers on all Installation signs unless otherwise instructed by the KO/COR IAW IDG. The Contractor shall place on all signs a unique identifiable, non-removable tracking number. The tracking number shall cross-reference the DMO number and listed in a log that identifies the location where the sign as installed.

    - Type of Paint. The Contractor shall use paints and coatings as recommended by the Unified Facilities Criteria (UFC) 3-120-01 and IDG. Munitions and hazardous material storage signs shall be color coded as required IAW IDG.

    - Traffic Sign Material Specification. The Contractor shall use High Intensity Grade Prismatic Reflective Sheeting for all traffic signs (ASTM Type IV or better). The Contractor shall use Telspar posts for high visibility traffic signs, due to the suitable breakaway or yield design. The Contractor shall fabricate traffic signs IAW the regulations on traffic signs.

    - Traffic Signs. Traffic signs which are taken down for repair shall be replaced immediately so as to avert accidents. All repairs and installations shall be IAW the MUTCD.

    - Informational Signs. The Contractor shall paint special signs such as facility or building numbers, street signs, directional signs, regulatory signs; individual group reserved parking signs, safety signs, boundary signs, fire prevention signs, physical and classified activity access signs, control signs, off limit signs, restricted area signs, medical activity signs, and special events signs. All signs shall be IAW applicable Regulations, IDG and the UFC.

    - Directional Signs. Directional signs shall be constructed of Polyester Laminated Resin half (1/2) board, covered with High Intensity Brown Reflective Sheeting, and letters shall be cut from Engineer grade white reflective sheeting material. The back of the board shall be painted mocha brown, and the poles shall be made of three inch (3”) square aluminum and 3/4” aluminum angle iron. All colors shall conform to current Information Management Association (IMA) standards.

    - Inspect and Survey. The Contractor shall inspect and survey traffic control signs and street-name signs, take corrective action and record this work as PMO work.

- Utility Systems.  The Contractor shall perform maintenance and repair of secondary (customer-side) utilities and primary systems still owned by the Government, non-potable water wells and systems, storm water collection systems, propane distribution system, and associated structures and appurtenances. The Contractor shall perform services as required herein to provide complete maintenance of utility systems and shall employ Root Cause Analysis methods of problem solving and deliver workable options to the KO/COR for consideration. The Contractor shall conduct all phases of work to comply with all applicable current Federal, State, and local regulations and operating permits including, but not limited to, current and future regulations listed in PWS 10, Energy and Utilities Service PWS. The Points of Demarcation to the commercial source and applicable standards of each utility is delineated in PWS 10, Energy and Utilities Service PWS.

  - Electric Distribution System. The Contractor shall be responsible for secondary non-privatized electric distribution system components which includes, but is not limited to, circuit breakers, batteries and battery chargers, transformers, street lighting systems, control systems, underground and overhead power lines, and electric meters. Work shall be completed IAW NFPA 70. The Contractor shall contact the RFAAP Government Staff for coordination with the utility provider.

    - Distribution Lines and Power Manholes. The Contractor shall perform all repairs to the existing secondary/customer-side power lines and to all wiring supporting street and perimeter lighting as required. The Contractor shall perform repairs to power manholes within the existing systems and perform repairs to manholes and vaults servicing the underground cable system. Where feasible, the Contractor shall repair, maintain, and modify the drainage of the distribution system, including but not limited to all manholes, hand holes, duct bank, drains, sump pumps, weep holes, and covers in order to maintain a clean, well ventilated, and moisture free environment to reduce corrosion of electrical connectors. The Contractor shall be certified IAW the Confined Space Entry Regulations.

    - Control Devices. The Contractor shall check the operation of the controls, repair or replace worn and broken parts, and tighten any loose connections.

    - Transformers. The Contractor shall observe and record the ambient temperature, liquid temperature, winding temperature, load current, voltage, tank pressure gauge, and liquid level. The Contractor shall check for loose electrical connections, contaminated bushings, oil leaks, ground resistance, and the operation of the auxiliary cooling fans. The Contractor shall also check butyl or porcelain surfaces, bushings, and grounding straps for wear, integrity, and breakage.

    - Relays. The Contractor shall clean the exterior and interior of the relay cases and covers. The Contractor shall also check and repair the internal components and contacts.

    - Circuit Breakers. The Contractor shall check and repair all contacts, insulation, arc chutes, and cleanliness of the operating mechanism on air circuit breakers. The Contractor shall check oil levels, correct fusing, the condition of bushings and terminals, oil leaks, dents, corrosion, and grounding on oil circuit breakers. The Contractor shall check the air compressor, tank, piping, valves, pressure switches, gauges, and solenoids on pneumatic systems.

    - Corrosion Protection. The Contractor shall perform corrosion inspection and corrosion protection of electrical equipment and related structures such as transformers, switches, switchgear, steel supports, concrete foundations, prefabricated structures, security fences, and grounding.

    - Network Enterprise Center (NEC) manholes. The Contractor shall perform repairs to NEC manholes within the existing systems and perform repairs to manholes and vaults servicing the underground cable system. Where feasible, the Contractor shall repair, maintain, and modify the drainage of the distribution system, including but not limited to all manholes, hand holes, duct bank, drains, sump pumps, weep holes, and covers in order to maintain a clean, well ventilated, and moisture free environment to reduce corrosion of communication cables and connectors. The Contractor shall be certified IAW the Confined Space Entry Regulations.

- Area Lighting.  PM and repair of non-privatized area lighting that is pole mounted and fed directly by the exterior electric distribution system, e.g., street and parking lot lights. Street lights and their circuits will be repaired and maintained as needed. This includes exterior building lights, typical street lights and parking lot lights.

  - Traffic Controls General. The Contractor shall be responsible for the repair and maintenance of all traffic signals, school zone flashers, street lights, pedestrian crossings, and solar/battery powered fixtures and devices. Reference TE, List of Traffic Signals. The Contractor shall semi-annually perform PM on traffic light controller devices listed.

  - Repair and Maintain Traffic Signals and Flashers. The Contactor shall repair and maintain Traffic signals and school zone flashers IAW the current edition of the MUTCD. Repair and maintenance also includes timing, reprogramming, adjusting and other tasks required in order to maintain safe operations for the driving public.

  - Preventive Maintenance Requirements. The Contractor shall develop and implement a PM plan for traffic signals and streetlights and submit for approval to the KO/COR with-in fifteen (15) calendar days of the start of the contract (CDRL A07-01). The Contractor shall inspect, take corrective action, and record this work as PMO work.

- Utility Marking. The Contractor shall be responsible for line spotting and marking underground non-privatized electric, water, sewer, propane, and gas lines as required by DMO. The Contractor shall also be required to locate cathodic protection anode beds, test connection points, valves, and other known underground structures as necessary IAW applicable laws, regulations, and color codes. The Contractor shall locate and mark underground utilities with spray paint or other suitable markers approved by the National Utilities Code of Color for Individual Underground Utilities in order to prevent damage when others are digging, installing, altering, or maintaining systems near existing underground utility systems. Prior to digging, the Contractor shall obtain a digging permit from the RFAAP Government Staff.

- Pumps and Pumping Stations. The Contractor shall perform maintenance procedures on all pumps. The Contractor shall visually check all pumps and motors for proper operation. On a monthly basis at all pumping stations, the Contractor shall flush and grease pumps and motor bearings and measure bearing temperatures.

  - Sewage Lift Stations. The Contractor shall perform the following on all mechanical and electrical lift stations:

  - Lift Station Inspection. The Contractor shall inspect the lift stations daily. The Contractor shall clean any bar screen, start the pumps, and check for smooth operation. Waste material removed from the bar screens and wires shall be disposed of properly to prevent any accumulation of odors.

  - Wet wells. The Contractor shall inspect the wet well at each lift station daily (normal duty work days) and clean as necessary. Any sediment from cleaning the wet wells shall be disposed of IAW applicable Location Name regulations. The fuel residuals shall be pumped out of the wet wells and disposed of in the same manner as the by- products from the oil/water separators. Cleaning shall include: removing grease, scum, and floatables from water surface and operating pumps to drain wet wells; hosing down the wet well interiors to remove all grease, scum, grit, or other foreign materials; and repairing wet well and pump components as necessary.

  - Pump Alternation. The Contractor shall alternate RFAAP Water Systems Lift Station pumps and its properties from lead to lag positions on a monthly basis to ensure even wear on all pumps, where applicable.

  - Storm Drainage Systems. The Contractor shall utilize and comply with the Water Environment Federation Manual for safety and record keeping and shall comply with all applicable Federal, State, and Army health and environmental standards in performing storm water services.

  - Flood Control Maintenance. The Contractor shall inspect all flood control pump stations for proper operation, cleanliness, and drainage twice a week and provide a copy of the inspection report weekly to the KO/COR as requested.

  - Survey all storm drainage systems. The Contractor shall survey and document the condition of all Storm Water Systems and associated parts on a bi-annual basis and provide a copy of the inspection report bi-annually to the KO/COR along with a plan of required corrective actions (CDRL A07-10).

  - The Contractor shall remove all debris and vegetation that has grown or accumulated in Contractor-controlled areas. Cleaning shall include, but is not limited to, the removal of sand, gravel, rocks, debris, trash, roots, sod, weeds, grass trapped within the lines, manhole chambers, culverts, and curb catch basins.

- Natural Gas and Propane Distribution System. The Natural gas distribution system includes only secondary non-privatized natural gas lines outside the footprint of a building or structure up to the point of demarcation with the primary utilities owned by the privatized utility contractor. The Points of Demarcation to the commercial source of each utility is delineated in the maps provided in PWS 10, Energy and Utilities. When not specifically noted in the maps it is with at the meter, the valve or five (5) feet from the building. Work shall be completed IAW NFPA 49, 49 CFR 192, and Transportation Guidance annual for Operation of Small Gas Systems. PM and repair of the natural gas distribution system and associated components, e.g., mains, service lines, and Cathodic protection. The Contractor shall maintain and repair all buried gas lines up to the point of demarcation. This includes services and lines between facilities or parts of facilities. The Contractor shall contact the DPW for coordination with the utility provider.

- Propane Tanks and Distribution Systems.  The propane gas and distribution system includes, but is not limited to, propane lines (steel/poly lines, both mains and laterals), propane tanks, meters, valves, and regulators. Most tanks are located in remote areas and Ranges to include Site Monitor. The Contractor shall ensure that all components of the Propane Gas Distribution Systems are maintained IAW 49 CFR Part 191 and 192, TM 5-652, TM 5-653, and other applicable State and Federal regulations. The Contractor shall maintain gas leak detection equipment in good operating condition at all times.

  - Gas Valves. The Contractor shall inspect and grease all gas valves annually for the Location Name propane distribution system, IAW 49 CFR Pipeline Safety Regulations 192.745 and 192.747.

  - Annual Leakage Survey. The Contractor shall perform an annual inspection on gas lines located on the Installation and its Ranges that are not owned by the privatized utility provider. The Contractor shall provide a copy of the annual inspection to the KO/COR (CDRL A07-10). The Contractor shall be responsible for making the necessary repairs determined by the class IAW 49 CFR 191 and 192.

  - Gas Regulator Caps. The Contractor shall inspect all gas regulators annually to ensure regulator caps are secured tightly and may not be easily removed. The Contractor shall replace any missing caps during the inspection.

  - Propane Tanks. The Contractor shall maintain the propane tanks free of corrosion and rust and paint as needed. When needed the Contractor shall relocate the tanks to locations as directed by the KO/COR. Relocating a tank may require evacuating the propane and refilling it. The Contractor shall provide any propane gas needed for testing if the tank is empty.

- Water Distribution Systems. This section only applies to secondary water system and some non-privatized primary water system components. The Contractor shall inventory, test, inspect, install, maintain, modify, and repair the non-privatized water distribution systems. The systems include, but are not limited to: water mains, water storage tanks, associated pumps, backflow preventers, fire loop fire hydrants, shut-off valves, pressure-reducing valves, and all other equipment to the buildings to which plumbing and piping are attached IAW UFC 3-230-02, O&M: Water Supply Systems; as applicable.

  - Secondary System. The Contractor shall maintain, repair, replace, install, inspect, re-move, and modify components of the secondary (customer-side) potable water systems to provide clean and safe potable water in adequate quantities and pressures for domestic use, fire protection, recreation, irrigation, and training purposes. The Contractor shall perform maintenance and repair on the potable (or non-potable) water distribution system IAW regulations. Whenever work on the potable water system is per-formed, the Contractor shall coordinate with the KO/COR and the privatized utility Contractor RFAAP Water Services Utility Provider. As required shall employ disinfecting method IAW AWWA C651-14, State Council on Environmental Quality and all applicable regulations that governing this type of work.

  - Water Lines. The Contractor shall maintain and repair all lines to maintain the integrity of the water distribution system. The Contractor shall also locate new lines, pump out flooded areas, excavate (including asphalt and pavement and sidewalk removal, if necessary), backfill, and clean up all water spillage; erect barricades prior to excavating and remove them after backfilling; and thaw frozen potable water lines. Repairs include, but are not limited to repairs to service connections.

    - The Contractor shall be responsible for locating water line and lateral service leaks, shutting off the water, repairing the leak, and returning water lines to a safe and serviceable condition. In the event of a water main break, the Contractor shall repair, disinfect, and perform the necessary microbiological water tests before reinstating the water service IAW AWWA Standard C 651-14. The water main and lateral service shall not be returned to service until it meets compliance with (State polices and regulations).

    - The Contractor shall notify the affected facilities and advise the KO/COR about the status of the water. Information shall include street location, indication of how the break occurred, area affected by the water outage, and the Contractor at the job site. Additional descriptive information may be required.

    - Excavation and Backfilling. If excavation and backfilling are required, the Contractor shall erect barricades prior to commencement of work and remove them after the work is complete. Backfilling shall be accomplished with dry sand, pea gravel, or compactable dirt. The Contractor shall place components on sand or dirt compacted every two feet (2’) at ninety percent (90%) compaction. No gravel or rock larger than 1/2” diameter shall be allowed to contact the utility. The Contractor shall place, above the repaired utility, tracer wire and magnetic tape six to twelve inch (6” to 12”) in the backfill. Dirt from the excavation shall be removed from the area and disposed of IAW Local, State, and Federal Regulations. At the completion of the project, the Contractor shall restore the site to its prior existing conditions, e.g., paving, landscaping, or rock blanket.

    - Fire Hydrants. Upon receipt of valid work document, the Contractor shall exercise, inspect, replace, and repair fire hydrants on the high-pressure fire loops under this contract (inspection temperatures must be above forty degree Fahrenheit (40°F)). Inspection tasks include, but are not limited to, checking proper operation, adjusting tightness of nozzles, checking for cracked barrels, inspecting operating nuts and nozzle threads, lubricating operating nuts, lubricating or replacing broken or stripped stems or stem nuts, painting (IAW the Installation color code), and re-packing valve stems.

    - Out-of-Order Fire Hydrants. The Contractor shall, within one (1) hour, notify the Fire Department and the KO/COR of work that will place any fire hydrant(s) out of service and the approximate length of time the area is going to be affected. The Contractor shall keep and file the following: the time, the location(s), identification, number of fire hydrant(s), and chlorine residual readings for all flushing of dead ends. The Contractor shall make the file available to the KO/COR upon request and shall provide the file to the KO/COR at completion or termination of the Contract. The Contractor shall be responsible for placing an out-of-service tag on the effected hydrant(s). The tag shall not be removed until the hydrant(s) is placed back in service and the Fire Department has been notified of the status.

    - Valves and Valve Boxes. The Contractor shall maintain complete operability of the distribution system; repair, install, and replace valves and valve boxes to maintain integrity of the water distribution system; locate valves, shut off water, decontaminate water lines, turn on water, flush water lines, and restore to original condition. The water system’s valves generally consist of gate and butterfly valves. Valves range from half to sixteen inch (1/2” to 16”) in diameter. Repairs include, but are not limited to, valve stem packing, lubrication (using approved Federal Drug Administration (FDA) food approved grease for domestic water service), replacement of broken, stripped stems or stem nuts, and any other work necessary to return valves to correct operating condition.

    - Pumps and Pumping Stations. The Contractor shall check and replace mechanical seals to pumps or packing (gland), clean air relief valves, and perform all maintenance, repair, and installation of pumps and pumping stations as required. The Contractor shall grease all pump bearings with ball roller bearing grease on an as needed basis. All pumps shall be dissembled as needed for inspection of impeller, wear ring, sleeves, and shaft.

    - Corrosion Protection. Contractor shall perform corrosion inspection and protection of water systems equipment and related structures including, but not limited to, valve houses, cathodic protection units, valves, sectional valves, steel supports, concrete foundations, prefabricated structures, and grounding following industry standards.

  - Backflow Prevention Program. The Contractor shall implement a comprehensive Cross-connection Control and Backflow Prevention Program IAW the State of State, EPA, and Location Name Water Services requirements (CDRL A07-01). The Contractor shall test all components under this contract and provide results to RFAAP upon request.

  - Wastewater Collection System. This section only applies to secondary wastewater system and some non-privatized primary wastewater system components. The Contractor shall be responsible for the maintenance of the secondary (customer- side) wastewater collection system which includes: grease traps, septic sewer systems, oil-water separators, sand traps, oil skimmers and lift stations. As part of the PM include, oxidation ponds, which shall require maintenance for their surrounding grounds per-formed through DMO requests. These may be transferred to Location Name for operation and maintenance. Work shall be completed IAW AWWA 651-92, C 652-92; UFC 3-240-01; UFC 3-420-01 and UPC. The Contractor shall perform services that include inspection and maintenance of all Wastewater Collection System components.

  - Mains and Service Lines. The Contractor shall provide PM and repair of wastewater col-lection mains, service lines and all components, e.g., sewer manholes and sewage lift stations.

  - Replacing Pipe. The Contractor shall repair or replace damaged, broken, collapsed, or clogged drainage pipes by reopening pipe trench and repairing or replacing damaged or worn pipes. The Contractor shall excavate pavement to gain access to storm sewers or drainage facilities where required. The backfill to the excavation shall be compacted and the surfaced area returned to its original condition.

  - Sewage Lift Station for Septic Systems. The Contractor shall perform maintenance on sewage lift stations.

  - Manholes. The Contractor shall maintain and repair sewer manholes, including repairing or replacing caps, ladders, rings, covers, and interior linings; uncovering those covered by dirt and debris and raising top to ground level; and removal of grit, sand, and debris from manholes. Manholes shall be structurally sound, clean, and free of debris. Man-holes shall be covered with cast iron manhole lids. The Contractor shall, after rodding or cleaning sewer lines, remove all waste and debris that surrounds the manhole clean out area.

  - Sanitary System Maintenance. Grease Traps and Solid Waste Interceptors shall be maintained with procedures to prevent breakthrough to the sanitary sewers

  - Ordinances. The Contractor shall comply with the City, State Code of Ordinances for discharges into the sanitary sewer. All discharges from the Installation shall comply with City pretreatment standards.

  - The Contractor shall perform the work IAW the following:

    - National Plumbing Code, American National Standards Institute

    - State Plumbing Code

    - Uniform Plumbing Code

    - AWWA

    - National Fire Protection Association

    - American Society for Sanitary Engineering (ASSE)

    - UFC 3-600-01, UFC 3-230-03, UFC 3-240-02, UFC 3-570-06

    - EPA Drinking Water Regulations, Manuals, Pamphlets and Guide Specs

    - Cross Connection Control Program

    - Technical Manual (TM) 5-813-05

    - OSHA, Codes and Laws

    - Environmental Laws and Directives

    - AR 420-1, Army Facilities Management

    - National Fire Codes (20, 22, 24 and 26)

    - UFC 3-230-01, UFC 3-230-02 (supersedes TM 5 660 and TM 5 661), UFC 3-230- 06A, and UFC 3-240-01

    - Federal, State, and Local EPA Regulations

- Storm Water Collection System. The storm water collection system collects and discharges storm sewer runoff to storm sewer outfalls and drainage. The Contractor shall maintain, modify, inspect, and repair the storm water collection system that includes, but is not limited to: culverts, grates, catch basin inlets, manholes, outlets, swales, gutters, channels, terraces, underground pipe and conduits, inlets, junction structures, drop structures, chutes, energy dissipaters, and storm sewers. The Contractor shall utilize and comply with the Water Pollution Control Federation Manual for safety and record keeping and shall comply with all applicable Local, Federal, State, and Army Health and Environmental Standards in performing storm water services.

  - Contractor shall provide and install storm drain markers at each inlet location that is not marked. Contractor shall conduct inspections of all secondary containment berm valves on an annual basis to assure proper operation and set on the closed setting; place ser-vice orders as needed.

  - On a semi-annual basis, the Contractor shall inspect storm drains and gutters along all roads and unclog as necessary to prevent flooding on those roads. The Contractor is to pump trash and sediment as needed from the storm drain systems. Storm collection is detailed on the Basic information maps. All damages to road (dirt, paved; asphalt, concrete, or hard surfaced) shoulders that are necessary for maintenance, repair, and cleaning of storm drainage systems shall be repaired by the Contractor. The Contractor shall survey and document the condition of all Storm Water Systems and associated parts on a bi-annual basis and provide a copy of the inspection report bi-annually to the KO/COR along with a plan of required corrective actions (CDRL A07-10).

  - Excavation and Backfilling.  If excavation and backfilling is required, the Contractor shall erect barricades prior to commencement of work and remove them after the work is complete. Backfilling shall be done with dry sand or compactable dirt and placing components on sand or dirt compacted every two feet (2’) at 80% compaction. No gravel or rock larger than half inch (1/2”) diameter shall be allowed to contact utilities. The Contractor shall dispose of waste from excavation at an approved off-post location. The Contractor shall restore the area to its original condition.

  - Storm Water Collection Main Repair. The Contractor shall repair, install, modify, or re-place all storm water collection mains to preserve the integrity of the storm water collection system. The Contractor shall be responsible for locating storm water collection main leaks, pipe repairs, and returning storm water lines to serviceable condition. The Contractor shall check the Storm Water Collection System during excessive rainfall to identify problem areas. Repairs must be approved by the KO/COR.

  - Catch Basins. The Contractor shall clean catch basins, drop inlets, open flumes, man-holes, and similar structures based on rate of silting or clogging with debris in order to ensure proper runoff. When entry into a structure is necessary, the Contractor shall comply with the Confined Space Entry Regulations. The Contractor shall maintain headwalls to prevent erosion or scour of the embankment adjacent to culvert inlets or outlets. No catch basin shall remain out of service longer than seven (7) calendar days.

  - Storm Sewers/System. The Contractor shall remove all debris, vegetation, and sediment that has accumulated in open above ground and enclosed below ground drainage conveyances in the areas designated. Cleaning shall include, but is not limited to, the removal of sand, gravel, rocks, debris, roots, sod, grass trapped within the lines, man-hole chambers, culverts, and curb catch basins. The Contractor shall treat sewer lines for grease as required.

- Preventive Maintenance of Storm Water Systems. The Contractor shall provide PM of all pipes, culverts, conduits, headwalls, drop boxes, grates, and open concrete lined channels, ditches, manholes, curb inlets, and all Storm Water Collection Systems. Water Services Utility Provider is the private utility provider however the storm water collection system is not privatized and the repair and maintenance of these systems shall be accomplished under this contract. The Contractor shall contact the DPW for coordination with the utility provider. Contractor shall provide maintenance schedule to Storm Water Program Manager on an annual basis (CDRL A07-01).

  - The Contractor shall maintain the storm water collection and treatment system to ensure continuous, normal operation. All ditches and culverts shall be free flowing and free of obstruction. Ponding shall not occur in culverts and drainage ditches. The Contractor shall employ erosion control measures on slopes that have been cleared of vegetation.

  - The Contractor shall schedule and inspect all systems and components for the Storm Water Collection System. The Contractor shall operate, monitor, maintain, and repair the storm water collection system and components IAW TM 5-820-4, Drainage for Are-as Other Than Airfields; TM 5-814-2, Sanitary and Industrial Wastewater Collection; Pumping Stations and Force Mains; AR 200-1, Environmental Protection and Enhancement; and, AR 420-1, Army Facilities Management. The Contractor shall submit to the KO for approval, within thirty (30) days of award, a plan for accomplishing the Storm Water Collection System maintenance work described in this Technical Exhibit. The Contractor shall inspect all flood control pump stations for proper operation, cleanliness, and drainage twice a week and provide a copy of the inspection report to the KO/COR upon request.

  - Storm Sewers. The Contractor shall remove, install, and replace storm sewers, grates, drop inlets, and covers as necessary. Any Contractor personnel entering a Storm Water Collection System shall comply with all requirements in the Confined Space Entry Regulations.

  - Compliance. While performing any work on utility systems, the Contractor shall comply with all applicable Federal, State, and local laws, Army regulations, standard industry codes.

  - The Contractor shall perform the work IAW the following:

    - National Plumbing Code

    - American National Standards Institute

    - Uniform Plumbing Code

    - Clean Water Act (CWA)

    - Unified Facilities Criteria (UFC) 3-230-02

    - Army Regulation (AR) 200-1, Environmental Protection and Enhancement

    - Manuals, pamphlets and guide specs

    - Occupational Safety and Health Administration (OSHA)

    - Industry standards

- Fuel Storage and Distribution Systems. The Contractor shall perform PM and repair the fuel distribution system. The fuel distribution system includes, but is not limited to, fuel distribution lines, underground and above ground fuel storage tanks, single wall tanks, receiving stations, leak detection and monitoring systems, and gaseous fuel storage and distribution. The Contractor will provide location of all fuel storage and distribution systems annually and perform monthly and annual inspections of all Single Wall Tanks and Above Ground Tanks on the installation, provided to the KO/COR Quarterly (CDRL A07-10).

  - The Contractor will perform monthly walkthrough inspections and annual inspections on Above and Under Ground Tanks.  Accurate records will be maintained on results IAW state and federal requirements. During walkthrough inspections, the Contractor will perform any limited cleaning of sumps, spill buckets and associated equipment, such as removing water from sump coverings/spill buckets, absorbing minor fuel puddles, etc. The Contractor will be responsible for ensuring as-signed A/B License Technicians are conducting these inspections and updated roster is always on file in with the copy of license. Work shall be completed IAW EPA Standards and Installation Spill Contingency Plan.

- Water Standpipes. The Contractor shall repair and maintain all water standpipes that normally supply non-potable water for use by Military units and other authorized Contractors. Contractor shall be required to lock standpipes to prevent unauthorized use and make arrangements to provide access to authorized users.

- Fire Loop System Hydrants. The Contractor shall maintain and repair fire loop systems, hydrants and associated components. The Contractor shall ensure hydrants are reliable and functional. The Contractor shall replace fire hydrants and gate valves as required. Replaced fire hydrant shall be equipped with firefighting adapters that are compatible with the Fire Department’s equipment.

  - Flow Testing. The Contractor shall coordinate hydrant flow testing operations with both the Fire Department and the KO/COR. The Contractor shall mark/paint hydrants according to the flow test results as required by NFPA 72 and NFPA 25. The Contractor shall record and report any malfunctioning hydrant to the KO/COR within twenty-four (24) hours of identifying the malfunction. The Contractor shall provide to the COR the metered quantity of water used while flushing or provide calculated quantity. Provide calculation method to determine quantity of water used.

  - Backflow Preventers. The Contractor shall submit for approval to the KO, a pro-gram to annually inspect, certify, repair, and perform PM on all backflow prevention de-vices under the contract. The Contractor shall inspect, test, and certify all backflow prevention devices operate IAW the American Water Works Association (AWWA), Environmental Protection Agency (EPA), State, and local compliance codes. The Contractor shall report any backflow prevention devices that are absent, inoperable, or non-certifiable, to the KO/COR within twenty-four (24) hours of identifying the defect. The Contractor shall meet all Safe Drinking Water Act (SDWA) regulations. The Contractor shall comply with the Cross Connection Program, preventing connection between potable and non-potable water systems and ensure approved protective devices are operational to prevent backflow between systems. The Contractor shall maintain documentation of all records and make them available for Government inspection within one hour of being notified. The Contractor shall maintain accurate changes to as-built drawings of new and modified installations regarding backflow prevention devices. The Contractor shall maintain records of Backflow test results, Customer Service Inspections, Technician training, and gauge calibration.

## Army Dams, Transportation and Infrastructure (ADTIP)

## Railroads.

    - General. The contractor shall follow all standards set forth in UFC 4-860-03.  The standards in this UFC protect investments in track maintenance and rehabilitation to ensure that DOD’s railroad track is maintained above those requiring restriction as stated in UFC 4-860-03.  The standards in UFC 4-860-03 provide maintenance standards for each possible type of deficiencies addressed in the Federal Railroad Administration Track Class 2 safety standards and adhere to additional speed restrictions.

    - Inspections. The contractor shall complete all inspections IAW UFC 4-860-03 and include as part of (CDRL A07-10).

## Bridges

    - General. The contractor shall follow all standards set forth in UFC 3-310-08.   UFC 3-310-08 was created to consolidate evolving federal bridge inspection and industry standards.  This UFC applies to all military installation bridges.  Installation bridges can be classified according to the type of traffic “over” the bridge as 1) highway bridges, 2) railroad bridges, 3) pedestrian bridges, 4) golf cart bridges, or 5) taxiway bridges. This UFC does not apply to expeditionary bridges located in military theaters of operation. This UFC does not apply to Army Corps of Engineers civil works bridges located outside of an installation.

    - Inspections. The contractor shall complete all inspections IAW UFC 3-310-08 and include as part of (CDRL A07-10)

## Vehicles

    - General. All General Service Administration (GSA) vehicles and other non-tactical vehicles (NTVs) that support personnel and product transportation, including but not limited to railcars, locomotives, powder vans, trucks, heavy equipment, ambulance, and fire engines shall be maintained in IAW AR 58-1.  Documentation of compliance of maintenance standards within this regulation with be provided to the USG upon request.

    - Lifting Equipment. All lifting equipment shall be inspected and tested IAW TB 43-0142. The Contractor shall develop, implement, and submit for approval to the KO/COR, a PM plan for inspection and annual load testing. Inspection requirements shall be derived from information provided by the lifting equipment manufacturer and TB 43-0142 and made part of (CDRL A07-10). Historical record of maintenance, inspections, and testing shall be recorded into the contractors CMMS and be provided to the government upon request.

## Applicable Directives, Publications.

  - ANSI A300		Standard Practices for Tree Care Operations

  - AR 58-1			Management, Acquisition, and Use of Motor Vehicles

  - AR 70-13		Management and Oversight of Service Acquisitions

  - AR 190-5		Motor Vehicles Traffic Supervision

  - AR 190-11	              Physical Security of Arms, Ammunition, and Explosives

  - AR 200-1		Environmental Protection and Enhancement

  - AR 200-3		Natural Resources; Land, Forest, and Wildlife Management

  - AR 200-5		Pest Management

  - AR 385-40 		Army Accident Investigation and Reporting

  - AR 405-45		Real Property Inventory Management

  - AR 405-70	              Utilization of Real Property

  - AR 420-1		Army Facilities Management

  - AR 420-70 		Facilities Engineering (Transportation Infrastructure and Dams)

  - AR 420-90		Fire Emergency Services

  - 29 CFR Part 1910 	Occupational Safety and Health Standards

  - 40 CFR			Protection of the Environment

  - 40 CFR Subchapter I	Solid Wastes

  - 40 CFR 257		Criteria for Classification of Solid Waste Disposal Facilities and Practices

  - 40 CFR Part 302		Protection of Environment, Designation, Reportable Quantities and Notification

  - Clean Air Act (CAA)

  - Clean Water Act (CWA)

  - DA PAM 385-40		Army Accident Investigations and Reporting

  - DA PAM 420-1-1	Housing Management*

  - DoD 4160.21-M		Defense Materiel Disposition Manual

  - DoD Directive 5500.7-R	Joint Ethics Regulation

  - DoDI 4150.07		DoD Pest Management Program

  - DoDI 5000.72		DoD Standard for Contracting Officer’s Representative (COR) Certification

  - EPA, Method 9095	Paint Liquids Filter Test

  - EPA, SW-846		Test Methods for Evaluating Solid Wastes, Physical/Chemical Methods

  - Federal Standard #313  	Material Safety Data and Disposal Data for Hazardous Materials Furnished to Government Activities

  - Federal Standard #595   Colors

  - FIFRA			Federal Insecticide, Fungicide, and Rodenticide Act

  - FIPS PUB 201-2		Personal Identity Verification (PIV) of Federal Employees and Contractors

  - HSPD 12		Homeland Security Presidential Directive 12 Policy for a Common Identification Standard for Federal Employees and Contractor

  - NFPA 1.12-2		Combustible Fibers

  - OPORD 13-153		Enterprise Municipal Services Performance Standards

  - SF 95			Position of Public Trust

  - TM 5-623		Pavement Maintenance Management

  - TM 5-624 		Maintenance and Repair of Surface Areas

  - TM 5-634		Solid Waste Management

  - TM 5-683		Electrical Interior Facilities

  - TM 5-820-4		Drainage for Areas other than Airfields

  - TM 9-6150-226-13 	Electrical Feeder System

  - UFC 1-200-01		DoD Building Code (General Building Requirements)

  - UFC 4-010-1		DoD Minimum Antiterrorism Standards for buildings (Change 1)

  - UFC 3-101-01		Architecture 11-28-2011

  - UFC 3-110-03 		Roofing, with Change 1 05-01-2012

  - UFC 3-110-04 		Roofing Maintenance and Repair 01-11-2007

  - UFC 3-120-01 		Design:  Sign Standards, with Change 2 03-01-2014

  - UFC 3-190-06 		Protective Coatings and Paints 01-16-2004

  - UFC 3-201-01 		Civil Engineering 06-01-2013

  - UFC 3-201-02 		Landscape Architecture, with Change 1 02-23-2009

  - UFC 3-210-10		Low Impact Development 07-01-2015

  - UFC 3-220-01 		Geotechnical Engineering 11-01-2012

  - UFC 3-220-04		Backfill for Subsurface Structures 01-16-2004

  - UFC 3-220-05 		Dewatering and Groundwater Control 01-16-2004

  - UFC 3-220-06 		Grouting Methods and Equipment 01-16-2004

  - UFC 3-220-08 		Engineering Use of Geotextiles 01-16-2004

  - UFC 3-220-10N 		Soil Mechanics 06-08-2005

  - UFC 3-230-01 		Water Storage, Distribution, and Transmission, with Change 2 11-01-2012

  - UFC 3-230-02 		O&M:  Water Supply Systems 07-10-2001

  - UFC 3-230-03 		Water Treatment 11-01-2012

  - UFC 3-230-06A 		Subsurface Drainage, with Changes 1-2 01-16-2004

  - UFC 3-230-13                   Industrial water Treatment operation and Maintenance

  - UFC 3-240-01 		Wastewater Collection, with Change 1 11-01-2012

  - UFC 3-240-02 		Domestic Wastewater Treatment 11-01-2012

  - UFC 3-240-03N 		Wastewater Treatment System Augmenting Handbook Operation and Maintenance 01-16-2004

  - UFC 3-240-05A 		Solid Waste Incineration 01-16-2004

  - UFC 3-240-10 		Soil Mechanics

  - UFC 3-240-11                   Landfills in Support of Military Operations

  - UFC 3-250-01FA 	Pavement Design for Roads, Streets, Walks, and Open Storage Areas 01-16-2004

  - UFC 3-250-03 		Standard Practice Manual for Flexible Pavements 05-15-2001

  - UFC 3-250-04 		Standard Practice for Concrete Pavements, with Change 2 01-16-2004

  - UFC 3-250-06 		Repair of Rigid Pavements Using Epoxy Resin Grouts, Mortars and Concretes 01-16-2004

  - UFC 3-250-07 		Standard Practice for Pavement Recycling 01-16-2004

  - UFC 3-250-08FA 	Standard Practice for Sealing Joints and Cracks in Rigid and Flexible Pavements 01-16-2004

  - UFC 3-250-09FA 	Aggregate Surfaced Roads and Airfields Areas 01-16-2004

  - UFC 3-250-11 		Soil Stabilization for Pavements 01-16-2004

  - UFC 3-270-01 		Asphalt Maintenance and Repair 03-15-2001

  - UFC 3-270-02 		Asphalt Crack Repair 03-15-2001

  - UFC 3-270-03 		Concrete Crack and Partial-Depth Spall Repair 03-15-2001

  - UFC 3-270-04 		Concrete Repair 03-15-2001

  - UFC 3-270-05 		Paver Concrete Surfaced Airfields Pavement Condition Index (PCI) 03-15-2001

  - UFC 3-270-06 		Paver Asphalt Surfaced Airfields Pavement Condition Index (PCI) 03-15-2001

  - UFC 3-270-08 		Pavement Maintenance Management 01-16-2004

  - UFC 3-280-01A 		Guidance for Ground Water/Fuel Extraction and Ground Water Injection Systems 01-16-2004

  - UFC 3-280-04 		Army Filtration of Liquids 12-17-2003

  - UFC 3-310-08 		Non-Expeditionary Bridge Inspection, Maintenance and Repair, with Change 1 08-16-2010

  - UFC 3-301-01                   Structural Engineering

  - UFC 3-320-06A 		Concrete Floor Slabs on Grade Subjected to Heavy Loads 03-01-2005

  - UFC 3-340-02 		Structures to Resist the Effects of Accidental Explosions, with Change 2 12-05-2008

  - UFC 3-401-01 		Mechanical Engineering 07-01-2013

  - UFC 3-410-01 		Heating, Ventilating, and Air Conditioning Systems, with Change 1 07-01-2013

  - UFC 3-410-02 		Lonworks (R) Direct Digital Control for HVAC and Other Local Building Systems, with Change 1 05-01-2012

  - UFC 3-410-04N 		Industrial Ventilation 10-25-2004

  - UFC 3-420-01 		Plumbing Systems, with Change 9 10-25-2004

  - UFC 3-420-02FA 	Compressed Air, with Change 1 05-15-2003

  - UFC 3-430-01FA 	Heating and Cooling Distribution Systems 07-25-2003

  - UFC 3-430-02FA 	Central Steam Boiler Plants, with Change 1 05-15-2003

  - UFC 3-430-05                   Natural Gas and Liquified Petroleum Gas Distribution Pipelines

  - UFC 3-430-07 		Operations and Maintenance:  Inspection and Certification of Boilers and Unfired Pressure Vessels, with Change 4 07-24-2003

  - UFC 3-430-08N 		Central Heating Plants 01-16-2004

  - UFC 3-430-09 		Exterior Mechanical Utility Distribution, with Change 1 01-16-2004

  - UFC 3-430-11		Boiler Control Systems 02-14-2001

  - UFC 3-440-01 		Facility-Scale Renewable Energy Systems 07-01-2015

  - UFC 3-440-05N 		Tropical Engineering, with Changes 1-2 01-16-2004

  - UFC 3-450-01 		Noise and Vibration Control 05-15-2003

  - UFC 3-470-01 		Lonworks (R) Utility Monitoring and Control System (UMCS) 05-01-2012

  - UFC 3-460-03 		O&M:  Maintenance of Petroleum Systems 01-21-2003

  - UFC 3-501-01 		Electrical Engineering, with Change 3 02-03-2010

  - UFC 3-490-06                   Elevators

  - UFC 3-520-01 		Interior Electrical Systems, with Change 3 02-03-2010

  - UFC 3-520-05 		Stationary Battery Areas, with Change 1 05-01-2015

  - UFC 3-530-01 		Interior and Exterior Lighting Systems and Controls 04-01-2015

  - UFC 3-540-01 		Engine-Driven Generator Systems for Backup Power Applications 08-01-2014

  - UFC 3-540-07                   Operation and Maintenance: Generators

  - UFC 3-550-01 		Exterior Electrical Power Distribution with Change 1 02-03-2010

  - UFC 3-550-07                    O&M: Exterior Power Distribution Systems

  - UFC 3-555-01N 		400 Hertz Medium Voltage Conversion/Distribution and Low Voltage Utilization Systems 01-16-2004

  - UFC 3-570-02A 		Cathodic Protection 03-01-2005

  - UFC 3-570-02N 		Electrical Engineering Cathodic Protection 01-16-2004

  - UFC 3-570-06 		O&M:  Cathodic Protection Systems 01-31-2003

  - UFC 3-575-01 		Lightning and Static Electricity Protection Systems 07-01-2012

  - UFC 3-580-01                   Telecommunications Interior Infrastructure

  - UFC 3-601-02 		Operations and Maintenance:  Inspection, Testing, and Maintenance of Fire Protection Systems; 09-08-2010

  - UFC 4-021-01		Mass Notification Systems

  - UFC 4-860-01                   Railroad Design and Rehabilitations

  - UFC 4-860-03                   Railroad Track Maintenance Standards