## QCIM
Q&A Solicitation 040ADV-26-R-0012
Questions | Answers
If known, when is this project expected to go to bid for contractors and what is the expected start date for construction? | This amendment extends the proposal due date to May 1, 2026. Please review Section F.3 Period of Performance of the solicitation for an expected construction start date.
Is the wall along column-line N near the property line? If so, exhausting to public space is not in compliance DC codes. | No, the wall along column-line N is not situated near the property line.
Is the existing exhaust ductwork appropriate for fume exhaust? Will acceptable velocities be able to be maintained. In general fume hoods require dedicated ductwork and discharges. | The exisiting ductwork is acceptable for fume exhaust.
How is the plumbing to be demolished associated with the bathroom? | Bathroom fixtures must be capped and abandoned, and all fixtures removed. Most bathroom fixtures are already capped and abandoned. The contractor shall ensure that they remain capped and abandoned during the installation of the new floor. Contractor can provide recommendations during design phase.
Is sanitary to be cut below slab, capped and abandoned in place? | The plumbing is to be capped and abandoned, and all fixtures removed. The shower that has been covered up may require to be cut below. Contractor can provide recommendations during design phase.
Does the vent piping serve any other areas that need to be maintained? | Yes, the vent piping serves other areas.
Does the domestic water piping serve any other areas that need to be maintained? | Yes, the domestic water piping serves other areas.
What is the extent of the bathroom ductwork removal noted photos and drawing F6101? Storage will likely require exhaust, depending on what is being stored. Please confirm. | The ductwork in the bathroom will be left alone - this is how the space's air will be maintained. Storage will not require exhaust.
Define demolition for hot water piping associated with the radiator. As this is the building exterior, will new heating be required? | Based on the conceptual design, the radiator shall be removed. However, it will need to be replaced with an equivalent heating source.
What integration and interconnection is required for the new security camera and card swipe? | The following is required when applicable: a card reader is required at door entry. Door monitoring switch in the door jamb. Request to Exit (REX) above the exit side of the door. The REX can be wall or ceiling mounted if a standard 8' suspended ceiling will be utilized. The contractor shall run conduit out of the wall above the ceiling height. In the case of a sliding door that has a card reader, there must be a locking mechanism and a way to release the door from the inside (button, "out" reader, etc.) For in-and-out readers, a REX is not required.
How far is the electrical power run, i.e. where is the panel with the ‘available circuits’? | Assume the panel is located outside of B544. If necessary, there is also an electrical shaft located on the other side of the elevators that can be pulled from.
Are there plumbing drawings showing the existing sanitary piping so the amount of concrete demolition will be required to accommodate the new tub sink? | No, there are no available drawings showing the existing sanitary piping.
For Volume III Past Performance - Out of the 5 projects is there a certain number of Design Build Projects that the government would like us to submit? | The goal of the past performance is to portray as much familiarity with the scope of work and project size as possible. There is not a set number of design build projects that the government requires to be submitted.
For Volume III Past Performance - For the statement of projects with similar scope and size. Is the size portion referring to a dollar value? | The dollar value is one aspect that the government considers when reviewing size. Other aspects include the complexity of actions being completed and the duration for completing these actions.
For Volume IV- For the Excel workbook is there a template or specific format to be used for this item? | No, there is no template or specific format to be used for this item.
A list of equipment used in the space. | Equipment in the space includes bookshelves, adhesives, and security cages - all provided and installed by GPO.
A list of chemicals used and stored in the space | Aside from adhesives, there are no chemicals stored in the space. The adhesives do not require any special conditions.
Name and contact of the HVAC Controls Company for the building. | Contact information will be provided post-award.
Please provide a picture and/or more information on the relocated tub sink from Building D, 2nd floor. Plumbing – F-6101 | That sink will no longer be used. Specifications for the tub sink will be determined during design phase.
Provide available structural, architectural, life safety, HVAC, plumbing, fire, electrical, technology as built information. ALL – F-6101 | There are no as-built drawings available for the space.
Drawing F-6101 indicates an existing exhaust fan in room B543 at the window while the new work view indicates a new exhaust fan for the mixer. Please clarify. MECHANICAL – F-6101 | Drawing F-6101 indicates that GPO desires for a new exhaust fan to replace the old one in the same location
Please provide make and model number of the new mixer. ELECTRICAL – F-6101 | The mixer is SPXFlow Lightnin, MODEL NO. X5P100
Please clarify what powered devices will be used at the electrical strips on the tables in room B543. ELECTRICAL – F-6101 | Standard scaling devices for measuring various substances will be used at the electrical strips on the tables in room B543.
For ventilation and fire protection purposes, please clarify what will be stored in room B541. FIRE – F-6101 | Adhesives will be stored in B541. No other chemicals will be stored in the space as GPO has flammable chemical shelves and dry chemical storage in a separate location. In the planned space B541A (secured storage), only documents are planned to be stored in the space.
Please provide the required exhaust/ventilation airflow for the new mixer. MECHANICAL – F-6101 | The existing system is acceptable regarding exhaust/ventilation airflow.
Provide additional information for the metal shelves indicated in B541. Please clarify quantity of shelves (spacing between shelves), material, and type (wire mesh, solid, etc.). ARCHITECTURAL – F-6101 | The metal shelves indicated in B541 will be provided and installed by GPO.
Please confirm the existing water connection to the emergency eye wash and shower fixtures is tepid water between 60–100°F. Plumbing – F-6101 | Yes, the existing water connection to the emergency eye wash and shower fixture is tepid water between 60-100°F.
Please provide camera requirements and information on the existing system which the camera must tie into. SECURITY – F-6101 | GPO requires a POE connection for cameras - a Cat5/6e cable to the nearest Main GPO network switch, to be determined by the IT department.
Confirm new lighting should be installed per ASHRAE 90.1-2019. ELECTRICAL – F-6101 | GPO does not formally adhere to ASHRAE 90.1-2019. Discussions during the design phase may be appropriate. Regarding occupancy sensors, providing LED lighting with a wall switch is sufficient for the space's requirements.
Are there additional security requirements for B541A Lab Secure Storage (e.g., additional door lock or manbars in ductwork)? ARCHITECTURAL – F-6101 | Yes, manbars in ductwork is required.
Confirm press fittings for domestic water applications are acceptable. Plumbing – Site Walk | Yes, press fittings are acceptable for domestic water applications.
Confirm bidding teams should assume the existing HVAC system has sufficient capacity and no new conditioning or makeup air equipment will be required. MECHANICAL – F-6101 | Yes, the bidding teams can assume the existing HVAC system has sufficient capacity and no new conditioning or makeup air equipment will be required.
Please indicate required wall and ceiling finishes for B543, B541, and B541A. ARCHITECTURAL – F-6101 | The wall and ceiling finishes will be determined during the design phase.
Confirm if the opening in the window of the new Lab Secure Storage should be infilled or covered. MECHANICAL – Site Walk | Covered is acceptable.
States that doors to rooms B541 and B541A must allow forklift access. Conceptual drawings show 3'-0" wide swing doors. What size forklift (height and width) must pass through these doors? ARCHITECTURAL – C.3.3.b. and F-6101 | Forklifts will not require access to the secure storage room B541A. However, the current intent is to install a sliding door into the B541 storage room, rather than the swing door shown in the conceptual drawings. Consider the Hyster N35ZRS3 model or equivalent when considering height and width.
States that doors to rooms B541 and B541A are to be 1.5 in doors. Standard hollow metal doors are 1.75 in. Is this acceptable? ARCHITECTURAL – C.3.3.b. | Yes, this is acceptable. The contractor can provide recommendations during design phase. The important requirement is that forklifts can enter/exit the space.
Flooring in existing room T521 is to be demolished. Flooring is terrazzo with infilled areas. Please confirm intent is to remove terrazzo floor. ARCHITECTURAL – C.3.2.a. | The current intent is to demolish the terrazzo flooring and replace it with a concrete fill.
What types of chemicals will be stored and used within these spaces? The RFP calls for polished concrete flooring. Given the presence of potentially hazardous chemicals, should an industrial epoxy coating be required? ARCHITECTURAL – C.3.3.a. | Chemicals will not be stored in the space. The concrete flooring shall have a protective layer to prevent abrasion and other damages.
Does the building have a standard for door hardware and lock cores? Can that information be provided? ARCHITECTURAL | The hardware itself must be able to accept Corbin Russwin 6 pin large format cores. Other specifications can be determined during the design phase.
Please provide a list of applicable codes and standards for this project. Assumed ICC and NFPA. Are UFC codes applicable? GENERAL | UFC codes are not applicable. A discussion during the design phase with GPO and the design team must occur to determine which codes are applicable.
Toilet partitions to be demolished are marble slabs. Should they be removed and stored for reuse elsewhere? ARCHITECTURAL – Photos | The slabs must be removed intact and stored at GPO for reuse.
Does the new sliding door to the mixing room need to be airtight when shut? Does it require a vision lite? ARCHITECTURAL – C.3.3.c. | No, the mixing door does not need to be airtight when shut. Yes, the new sliding door does require a vision lite. The conceptual drawing for the storage room (B541) shows a swing door. The current intent is to also have a sliding door there that requires a vision lite. The sliding door for B541 does not need to be airtight either.
The existing interior partitions are brick or CMU. Should the new wall between B541 and B541A be CMU or a metal stud gypsum board partition? ARCHITECTURAL – C.3.3.e. and Photos | The wall can be a metal stud gypsum board partition. Recommendations can be provided during the design phase.
Confirm GPO #2032 mixer will be relocated and stored in B520 with no additional provisions required. ARCHITECTURAL – F-6101 | Yes, GPO will cover the rest of the necessary provisions for the relocation of the mixer. The Contractor may be asked to assist in relocating the mixer before construction begins.
Provide product data or basis of design for the Laboratory Fume Hood referenced in C.3.5. ARCHITECTURAL – C.3.5 | GPO has acquired a Protector XL Laboratory Hood. Please see User's Manual attached.
Please provide the required climate control and temperature conditions for all applicable spaces. Are there any special provisions? MECHANICAL – C.3.4 | No special provisions are required. The rooms shall be within the standard temperature range of 70° F (± 5° F).
The HVAC system appears to be single-zone. Will it provide minimum heat 24/7, or will auxiliary heaters be required for each space? MECHANICAL – C.3.4 | Minimum heat will not be provided 24/7; auxiliary heaters will be required for all spaces.
Please provide additional requirements for the tables shown in B543. ARCHITECTURAL – F-6101 | GPO will provide the tables shown in B543.
Is any specialty lighting required (e.g., true color rendering or high brightness)? ELECTRICAL – F-6101 | No, there is not a requirement for speciality lighting.
Which panelboard should be used for the renovation? Has it been evaluated for load and capacity? ELECTRICAL – F-6101 | Assume there is an electric panel on the outside wall of B544. It has not been evaluated for load and capacity.
Are there any special storage requirements such as humidity control, freezers, or refrigerators? ELECTRICAL – F-6101 | No, there are no humidity control, freezer, or refrigerator requirements.
Are there any requirements for a small batch or additives prep area? ELECTRICAL – F-6101 | No, there are no requirements for a small batch or additive prep area.
Does any equipment or storage system require uninterruptible power (UPS)? If so, for what duration? ELECTRICAL – F-6101 | No, no equipment or storage system requires uninterruptible power.
Is there a QC requirement for mixed product? Does this require a separate area or test equipment? ELECTRICAL – F-6101 | No, there is not a QC requirement for mixed products, and a separate area or test equipment is not required.
Is any special transport equipment required (forklift, self-powered cart, crane)? Are any charging stations required? ELECTRICAL – F-6101 | Charging stations are not required. Equipment such as forklifts, should be able to be used in the space.
Are any special communication networks required? ELECTRICAL – F-6101 | No, there are no special communication networks required.
SF 1442 indicates a bid bond is not required. Please confirm. | A bid-bond is required. The Government will update this with an amendment.
Factor #2 Key Personnel - Please confirm the PM/QC and/or Superintendent/Safety Lead may dual hat provided the proposed individual meets the requirements of both proposed positions. | The Safety Lead must be single-hatted. The PM, QC, and Supertindent may be dual-hatted, but an individual cannot perform more than two of those roles.
Factor #3 Past Performance – Please confirm that “five (5) different customer references for projects” indicates 5 different evaluators, versus project examples from 5 different clients (i.e. 2 separate projects could come from the same client, as long as they have different evaluator points of contact completing the 2 project’s PPQs.) | Offerors may submit multiple projects from the same client, provided each project is distinct and meets the relevancy criteria. Each project must include a separate Past Performance Questionnaire (PPQ).