| SUBJECT* | 1.5MW Generator Rental |
| --- | --- |

GENERAL INFORMATION

| CONTRACTING OFFICE’S ZIP CODE* | 28301 |
| --- | --- |
| SOLICITATION NUMBER* | 36C24626Q0503 |
| RESPONSE DATE/TIME/ZONE | 04-10-2026 1:00PM EASTERN TIME, NEW YORK, USA |
| ARCHIVE | 60 DAYS AFTER THE RESPONSE DATE |
| RECOVERY ACT FUNDS | N |
| SET-ASIDE |  |
| PRODUCT SERVICE CODE* | 5999 |
| NAICS CODE* | 335312 |
| CONTRACTING OFFICE ADDRESS | Department of Veterans Affairs Network Contracting Office 6 201 Hay Street, Suite 304 Fayetteville NC 28301 |
| POINT OF CONTACT* | Contract Specialist Cedric Frasier cedric.frasier@va.gov |

PLACE OF PERFORMANCE

| ADDRESS | Central Virginia VA Health Care System |
| --- | --- |
|  | 1201 Broad Rock Blvd |
|  | Richmond VA |
| POSTAL CODE | 23249 |
| COUNTRY | USA |

ADDITIONAL INFORMATION

| AGENCY’S URL | https://va.gov |
| --- | --- |
| URL DESCRIPTION | va.gov |
| AGENCY CONTACT’S EMAIL ADDRESS | cedric.frasier@va.gov |
| EMAIL DESCRIPTION | va.gov |

DESCRIPTION

Sources Sought Notice: Generator Rental

Department of Veterans Affairs, Network Contracting Office (NCO) 6 Richmond VAMC

The Department of Veterans Affairs (VA), Network Contracting Office (NCO) 6, on behalf of the Richmond VA Medical Center, is conducting market research via this sources sought notice to identify qualified businesses capable of providing generator rental services that meet the requirements below.

Salient Characteristics

A. Required Function:

Provide rental of a generator that complies with National Fire Protection Association (NFPA) standards.

B. Required Performance:

Richmond VA Medical Center requires a temporary trailer-mounted generator (1500kW/1.5MW) to meet NFPA startup standards until a permanent solution is implemented.

C. Essential Physical Characteristics:

The rental generator must meet the following specifications:

Power Output: 1500 KW

Rating: 1750 KVA

Onboard Fuel: 0 gallons

Voltage: 480/277V, 3 phase

Frequency: 60 Hz

Fuel Capacity: 5,200 gallons

Trailer-mounted unit

Built-in fuel tank

Start-up assist feature

Ability to connect to existing critical power switchgear

All copper wiring

Compatible with current switchgear connection methods

Controlled by the existing generator control system

Include electrical drawings

Provided with galvanized rigid steel (GRS) conduit

Qualifications of Offerors:

Must be established in the required field, and provide appropriate licensing

Must be financially responsible and able to demonstrate reliability, experience, equipment, facilities, and personnel necessary to provide satisfactory service

Respondents are requested to provide the following information:

Indicate whether your business is a manufacturer or a reseller of a small business manufacturer

Specify your interest in submitting a Federal Supply Schedule (FSS) quote or Open Market quote (include FSS contract number, if applicable)

Identify any affiliated companies (wholly or partially owned) that provide similar goods/services under related NAICS codes, including CVE certification type (SDVOSB/VOSB), Federal Identification Number, and state of incorporation

Confirm active SAM registration and provide your Unique Entity Identifier (UEI)

Provide a current capabilities statement

Failure to supply this information may result in your company being considered incapable of fulfilling the VA’s requirements.

Additional Information:

This notice is for market research purposes only to inform the Government’s acquisition strategy. No questions regarding this notice will be entertained. The VA will not cover any costs associated with preparing responses to this market research.

The capability statements received from this market research are for planning purposes only and will assist the Government in planning its acquisition strategy. This is strictly market research, and the Government will not entertain questions concerning this market research. The Government will not assume any costs incurred by the contractor in the preparation of responses.  All responses shall be submitted in writing no later than April 10th, at 1:00 PM EST to the attention of:  Cedric.frasier@va.gov

Please title the subject line for all responses as: Sources Sought Generator Rental 36C24626Q0503.