Performance Work Statement

(Includes associated Performance Requirements Summary (PRS))

TURN-KEY INSTALLATION OF A SANDING BOOTH

PART 1

General Information

1.  General:  This is a non-personal service(s) contract under which the personnel rendering the service(s) are not subject, either by the contract’s terms or by the manner of its administration, to the supervision and control usually prevailing in relationships between the Government and its employees.

1.1  Description of Services/Introduction:  This is a non-personal service(s) contract to provide the turn-key design, engineering, supply, delivery, installation, assembly, set-up and training for a new crossdraft-style sanding booth in an existing building at the Tobyhanna Army Depot (TYAD), Tobyhanna, PA 18466.

1.2  Background:  A new Sanding Booth will provide Tobyhanna Army Depot (TYAD) capability to repair dents, holes, cracks, etc. in composite materials by applying epoxies and glazing compounds, and by performing wet lay-ups using carbon fiber, fiberglass and Kevlar.  The Sanding Booth will handle composite material repairs for the depot workload.  Epoxies and glazing compounds will be applied while wearing proper personal protective equipment, including coveralls, safety goggles and respirators with organic vapor cartridges.  The decibel (dBA) sound level of power sanding using a rotary grinder with vacuum attachment is 90-95 dB within the sanding booth enclosure.  A diagram of the proposed booth configuration is included under Attachment 3.  A dust sample from an existing TYAD sanding booth used for fiberglass sanding and repair was tested at EMSL Analytical, Cinnaminson, NJ for explosivity.  The dust sample was determined to be ‘explosible’ in dust form.  The explosion severity result (Kst) is 159 +/- 12%, which is considered Dust Explosion Class St 1, Weak Explosion.  The report from the dust explosivity test is included under Attachment 4.  Fiberglass repair work performed in the booth involves flammable glues or resins in large volumes; volatile organic compounds (VOCs) are a concern.

1.3  Scope:  The Contractor shall provide non-personal service(s).  The Contractor shall provide all personnel, equipment, supplies, facilities, transportation, tools, materials, consumables, labor, and supervision for the turn-key design, supply, delivery, installation, assembly, set-up and training to install a new crossdraft sanding booth as described in this PWS and associated contract documents, except for those items specified in Part 3 Government Property and Services. The Contractor shall perform to the standards and acceptable quality levels identified in this PWS and associated contract documents.

1.4  Objectives:  The objective of this contract is to provide a complete and fully functional, turn-key crossdraft-style sanding booth that meets all specifications and safety requirements outlined in this PWS.

1.5  General Information:

1.5.1  Quality Control Plan (QCP): The contractor’s existing quality assurance system shall be utilized in accordance with Revolutionary FAR Overhaul (RFO) 12.105, Quality requirements.

1.5.2  Quality Assurance:  The Government will evaluate the Contractor’s performance under this contract in accordance with the Quality Assurance Surveillance Plan (QASP). This plan is primarily focused on what the Government must do to ensure that the Contractor has performed in accordance with the performance standards. It defines how the performance standards will be applied, the frequency of surveillance, and the acceptable quality levels (performance thresholds).

1.5.3  Recognized Holidays:  The following provides information on recognized holidays for the purpose of the PWS.  If submittal of any documentation (e.g. deliverables, submittals, etc.) deadlines fall on a holiday, the closest work day prior to the holiday will apply as the deadline for submittal.

1.5.3.1  U.S. Holidays: Work shall not be performed on U.S. federally recognized holidays occurring during the normal workweek unless otherwise directed by the Contracting Officer. When a U.S. holiday occurs on a Saturday or a Sunday, the holiday is observed on the preceding Friday or following Monday, respectively.

New Year’s Day January 1st			M. L. King Memorial Day 3rd Monday in Jan

Presidents Day 3rd Monday in February		Memorial Day last Monday in May

Juneteenth June 19th                                          Independence Day July 4th

Labor Day 1st Monday in September                  Columbus Day 2nd Monday in October

Veteran’s Day November 11th                            Thanksgiving Day 4th Thursday in November

Christmas Day December 25th

1.5.4  Operating Hours:  The Government facility office hours, facility operating hours, and the Contractor support hour requirements often coincide, however, they may differ.  Please refer to the following.

1.5.4.1  Government Facility Office Hours:  The Government facility office hours are 0700 to 1630 Monday through Friday except U.S. Holidays identified in paragraph 1.5.3.1 above or when the Government facility is closed due to local or national emergencies, administrative closings, or similar Government directed facility closings.

1.5.4.2  Government Facility Operating Hours:  The Government facility operating hours occur between the hours of 0700-1630 Monday through Thursday and 0700-1530 Friday. The Government facility is The Government facility is open for operations during the recognized U.S. Holidays identified in paragraph 1.6.3.1 above. The Government facility may close due to local or national emergencies, administrative closings, or similar Government directed facility closings and will be communicated by the Contracting Officer to the Contractor.

1.5.4.3  Contractor Support Hours:  The Contractor shall provide support between the hours of 0730 to 1530 Monday through Friday.  The facility may close during local or national emergencies, administrative closings, or similar Government directed facility closings. The Contractor shall maintain an adequate workforce at all times, for the uninterrupted performance of all tasks defined within this PWS when the Government facility is not closed for the above reasons. When hiring personnel, the Contractor shall keep in mind that the stability and continuity of the workforce is essential.

1.5.4.3.1  Contractor Work Plan:  RESERVED

1.5.5  Training Holidays:  RESERVED

1.5.6  Place of Performance:  The work to be performed under this contract will be performed in Government facilities at TYAD, Tobyhanna, PA 18466.

1.6  Security Requirements:  Contractor personnel performing work under this contract must comply with all security requirements as detailed in this PWS. A specific security clearance is not required; however, background checks are mandatory.  See below for Security Requirements for All SOWs & PWSs (updated April 2026)

- Force Protection Condition (FPCON) Should the Force Protection Condition (FPCON) at the installation change, the Government may require changes in contractor security matters and/or processes.

If based on the requirements of this contract, contractor employees may be designated as mission essential. Mission-essential contractor employees are required to report for duty and remain on duty during declared emergencies and/or elevated FPCON levels unless otherwise directed by the Contracting Officer (KO) via the appropriate Contracting Officer's Representative (COR).

Unscheduled gate closures by Law Enforcement may occur at any time causing all personnel entering or exiting a closed installation to experience a delay. This cannot be predicted or prevented. Contractors are not compensated for unexpected closures or delays.

Vehicles operated by contractor personnel are subject to search pursuant to applicable regulations. Any moving violation of any applicable motor vehicle regulation may result in the termination of the contractor employee’s installation driving privileges.

The contractor’s employees shall become familiar with and obey the regulations of the installation, including law enforcement, fire, traffic, safety and security (protecting National security) regulations while on the installation. Contractor employees should only enter restricted areas when required to do so and only upon prior approval. All contractor employees shall carry proper identification with them at all times. The contractor shall ensure compliance with all regulations and orders of the installation which may affect performance.

The contractor, if required, shall provide support during contingencies, exercises, heightened operations, and adverse weather or security closures in the accomplishment of performance requirements. From time to time, the Base Commander may decide to close all or part of a base in response to an unforeseen emergency or similar occurrence. Such emergencies include adverse weather such as snow, or ice, "an act of God,” such as tornado or earthquake, or a base disaster such as a gas leak or fire.

- Emergency Communications and Services. If assigned to TYAD for (7) seven days or longer, contractors and subcontractor employees will enroll in the ALERT! Mass Warning Notification System (MWNS). Common Access Card (CAC) is required to register for ALERT!.  If a CAC has not been deemed necessary for the contractor or subcontractor, the COR will provide the necessary information to TYADs Antiterrorism Officer or TYADs Emergency Manager in the Security Operations Branch for manual input into the ALERT! System.

ALERT! MWNS is NOT optional - it is a Headquarters Department of the Army (HQDA) requirement to be a registered user.

Due to the life-safety implications of the information being relayed and the requirement to provide immediate alerts and warnings, personnel assigned to TYAD must ensure that their personal contact information, including after-duty hours contact information, as appropriate (e.g., personal cellular phone numbers or landline phone numbers), e-mail addresses, home address, etc., are entered into the system and regularly updated or verified every 90 days to remain current and accurate.

In the event of a life-threatening emergency or natural disaster, COR will account for assigned contractors. COR will send personnel accountability report to Emergency Operations Center (EOC).

Base closure announcements will be disseminated via ALERT! MWNS.

- Antiterrorism (AT) Level I Training.  In accordance with AR 525-13, all contractor and subcontractor employees requiring access to Army installations, facilities, or controlled access areas shall complete AT Level I awareness training annually. This training must be completed prior to being granted installation access and beginning work. The contractor is responsible for ensuring this requirement is met and for providing certificates of completion for each employee to the COR upon request. The web-based training is available at https://jko.jten.mil  (Course: JS-US007).

AT Level I and iWATCH training is not required to be in person.  While in-person training is an option, the most common and widely accepted method is web-based.  Army regulations explicitly provide multiple ways to meet the training requirement to ensure flexibility for all personnel, regardless of their location or access to a classroom setting.

- iWATCH Army Training. This training will be used to inform employees of the types of behavior to watch for and instruct employees to report suspicious activity to the COR. This training shall be completed within 30 calendar days of contract award and within 30 calendar days of new employees commencing performance with the results reported to the COR NLT 30 calendar days after contract award. Contractors and all associated sub-contractors will be briefed by the TYAD Antiterrorism/Force Protection officer. It is recommended this training be conducted as part of an initial entry briefing or unit/organization newcomer’s briefings. Send training requests to TYADs Antiterrorism Officer.  Contractor employee training will be documented on a local form.

- Access and General Protection/Security Policy and Procedures.  Contractor and all associated sub-contractor employees shall comply with applicable installation, facility and area commander installation/facility access and local security policies and procedures (provided by government representative). The contractor shall also provide all information required for background checks to meet installation access requirements to be accomplished by TYAD Law Enforcement. Contractor workforce must comply with all personal identity verification requirements as directed by DoD, HQDA, and/or local policy.

Contractor and all associated sub-contractor employees shall comply with adjudication standards and procedures using the National Crime Information Center Interstate Identification Index (NCIC-III) and Terrorist Screening Database (TSDB) (Army Directive 2014-05/AR 190-13), applicable installation, facility and area commander installation/facility access and local security policies and procedures (provided by the government representative), or, at OCONUS locations, in accordance with status of forces agreements and other theater regulations.

A background check and approval from TYAD Law Enforcement is required for all contractor and subcontractor personnel prior to on-site access at TYAD.  All persons seeking entrance to TYAD shall submit to and comply with all security standards and requirements in force at the time such persons are seeking entry.  All contractors, regardless of resident status or citizenship, will be subject to vehicle search and intense in-processing by TYAD security personnel prior to being granted access to TYAD.  This requirement is inclusive of on-site supervisory or managerial personnel and sub-contractor personnel that the contractor anticipates will be performing work or visiting on-site.  This security screening process may be time consuming, and access may be delayed or denied. COR will provide specifics to the contractor after award and at least ten days prior to the expected visit date for completion.  This security screening does not relieve the contractor of any responsibilities to conduct thorough pre-employment background checks and drug screening. Contractor workers will not be granted access to the work site until security screening is completed and access is approved.  Any contractor personnel on-site who fail screening will not be permitted further access to TYAD. Ensure undocumented workers are not included in contracted work related to Army missions.

The company will ensure that its employees entering Army-controlled installations or facilities have obtained access badges and passes in accordance with facility regulations and that these badges and passes are obtained in advance so as not to delay the accomplishment of contracted services.

- Pre-Bid Site Visit Controls: Any pre-bid site visits held before the contract award will be conducted under strict security controls. These protocols—including mandatory pre-registration for baseline vetting and constant escorting—apply to all potential bidders, regardless of any previous work history with TYAD or current installation access. During this public solicitation phase, a contractor's prior access or familiarity with the installation does not grant them a "need-to-know" for a new requirement. All bidders will be treated as external entities, and the site visit is strictly for a visual inspection of physical conditions only.

- Post-Award Information Release: Conversely, all project specifics—including exact locations, detailed plans, and mission context—can and must be provided to the contractor only after the contract is awarded and their personnel have completed all mandatory security training (AT, OPSEC, CUI). At this stage, the contractor has an established "lawful government purpose," and the controlled release of detailed information is appropriate and necessary for the performance of the contract.

Common Access Card (CAC): RESERVED

- For contractors that do not require CAC, but require access to a DoD facility or installation: Contractor and all associated subcontractor employees shall comply with adjudication standards and procedures using the National Crime Information Center Interstate Identification Index (NCIC-III) and Terrorist Screening Database (Army Directive 2014-05/AR 190-13); applicable installation, facility and area commander installation and facility access and local security policies and procedures (provided by Government representative); or, at OCONUS locations, in accordance with status-of-forces agreements and other theater regulations.

- Collection of Badges:  The Contractor shall account for all forms of Government-provided identification (even visitor badges) issued to the Contractor employees in connection with performance under this contract. The Contractor shall return such identification to the issuing agency at the earliest of any of the following, unless otherwise determined by the Government:

- When no longer needed for contract performance

- Upon completion of the Contractor employee’s employment

- Upon contract completion or termination

The Contracting Officer may delay final payment under a contract if the Contractor fails to comply with these requirements.  The Contractor shall insert the substance of this clause, including this paragraph, in all subcontracts when the subcontractor’s employees are required to have routine physical access to a federally controlled facility and/or routine access to a federally controlled information system. It shall be the responsibility of the prime Contractor to return such identification to the issuing agency in accordance with the terms set forth in of this section, unless otherwise approved in writing by the Contracting Officer.  The company will return all issued U.S. Government Common Access Cards, installation badges, and/or access passes to the COR when the contract is completed or when a contractor employee no longer requires access to the installation or facility. Contractor personnel will obtain a vehicle pass for access to the military installation and Common Access Cards for computer access, if applicable.

- Operations Security (OPSEC). OPSEC is mandatory for all and is not a one-time checklist; it is a dynamic, ongoing process embedded in every phase of planning, execution, and daily operations. It requires continuous critical thinking and vigilance from everyone who interacts with government information or operates on a government installation. This includes military personnel, Department of Defense civilians, contractors, subcontractors, and family members. OPSEC is not just a policy, it’s a mindset. Its success depends on consistent awareness and execution by every member of the TYAD community.

At TYAD, all observations, communications, and experiences must be protected and must not be shared with anyone lacking a lawful government purpose or a validated business need-to-know. This disciplined approach ensures that emerging threats, evolving vulnerabilities, and shifting mission parameters are constantly reassessed and addressed to safeguard critical information.

OPSEC applies across the full spectrum of DoD missions, functions, programs, and activities under this contract. Practicing OPSEC daily is a requirement that is essential to mission success and the protection of national security assets.

Failure to properly safeguard sensitive or classified information—whether through negligence, willful misconduct, or ignorance—may result in administrative, disciplinary, contractual, or criminal consequences.

Applicability and Management of the Contractor OPSEC Plan The requirement for an Operations Security (OPSEC) Plan or an OPSEC Standing Operating Procedure (SOP) is based on the contractor's access to and handling of Critical Information and/or Controlled Unclassified Information (CUI), regardless of where that information resides. It is essential to distinguish between Information Security (INFOSEC), which protects data "at rest" within a system, and OPSEC, which protects data "in use" by governing the procedures and actions of personnel.

When contractor personnel generate, access or handle CUI—such as building floor plans, maps, technical manuals, operational schedules, or documents that contain information that falls within a CUI category www.dodcui.mil—they are required to have an approved OPSEC Plan/SOP (Deliverable A.001).  Contact the COR for more information on an OPSEC Plan/SOP. This plan is a formal, documented agreement that outlines how the contractor will protect the government's sensitive information. Even when CUI is handled exclusively on Government Furnished Equipment (GFE), the contractor remains responsible for the "human factor." The OPSEC Plan transfers the responsibility for protecting this information from the Government to the contractor by legally obligating them to establish internal procedures for everything from secure physical storage and controlled discussions to the proper destruction of materials. Without this plan, the Government retains all risk for how a contractor safeguards its data.

The management and approval of the contractor's OPSEC Plan is a shared responsibility, with defined roles at each stage. Per government acquisition and security policy, it is the Contracting Officer's Representative (COR) who is ultimately responsible for the initial identification and final enforcement of this requirement. The process is as follows: The COR (designated technical representative) identifies the need for an OPSEC Plan based on the work described and writes the requirement into the PWS and checks this off on the Security Review Cover Sheet. After contract award, the COR enforces this by ensuring the contractor submits the plan on time. The Contracting Officer (KO) ensures the requirement is legally binding in the final contract and is the sole authority to take contractual action for non-compliance. Finally, the Government OPSEC Officer, as the technical expert, is responsible for reviewing the submitted plan against AR 530-1 and providing the formal approval or rejection back to the COR.

– Mandatory Annual OPSEC Training Requirements. In accordance with AR 530-1 (4-2-a), all contractors and subcontractors shall complete OPSEC Level I certification training annually (Initial and Continual – detailed below).

The Contracting Officer’s Representative (COR) serves as the oversight authority: the COR verifies contractual compliance by collecting and reviewing certificates, ensuring they’re submitted within the required timeframe – first 30 days of assignment.

According to AR 530-1 (para 4-2) and DoDM 5205.02, there is no “grace period” or minimum number of days on-site before OPSEC Level I Initial and Continual training becomes mandatory—any contractor, subcontractor, or support‐service provider who requires access to TYAD information, systems, or facilities must complete both parts of their OPSEC Level I training.

OPSEC Level I training is comprised of two parts (Initial and Continual):

- OPSEC Level I Initial training (annual):

  - To be completed within first 30 days of assignment to TYAD and annually thereafter – preferably before the job starts

  - Provides specific information about TYADs OPSEC program

  - Contractors and subcontractors must set up an appointment with TYADs OPSEC Officer for Initial training.  The COR will provide the necessary point of contact to schedule this training.

  - Conducted by TYAD’s OPSEC officer or alternate – training can be in person or via MS Teams (30 minutes) and is tracked by a TYADs OPSEC Officer via a local training form

- OPSEC Level I Continual training (annual):

  - Commonly referred to as annual OPSEC training

  - To be completed within 30 days of assignment to TYAD and annually thereafter – preferably before the job starts

  - Provides general information about OPSEC and reemphasizes sound OPSEC practices throughout the contract period

  - Title of the training is: “OPSEC Awareness for Military Members, DoD Employees and Contractors” and is available online - https://securityawareness.dcsa.mil/opsec/index.htm

  - Certificates of completion must go to the COR

- OPSEC Measures to Protect Critical Information.  All personnel are required to protect critical information at all times and in all forms.  This section is critical because it moves beyond a simple, vague requirement to “practice OPSEC” and provides the contractor with specific, actionable, and enforceable rules of behavior.

All contractors and subcontractors shall implement the following mandatory OPSEC measures during the entire period of performance to protect critical and sensitive unclassified information:

- Training and Compliance: Complete all mandatory OPSEC training as specified in this contract and actively apply all TYAD OPSEC measures in daily, contract-related operations.

- Secure Communications: Avoid discussing government operations in public spaces or over unprotected communications (e.g., personal cell phones). Transmit Controlled Unclassified Information (CUI) only through authorized, encrypted channels as directed in the SOW/PWS = DoD Safe Access File Exchange (SAFE, https://safe.apps.mil/) is the accredited method for sending files that contain CUI, Personally Identifiable Information (PII), or other sensitive data that should not be transmitted over unencrypted, commercial email channels. The files are encrypted during the transfer process.

- Public Release and Social Media Prohibition: Do not disclose or post any images, data, or operational details (e.g., maps, pictures, schedules, equipment, tactics) to any unofficial media, including personal or corporate social media platforms. All information or materials intended for public release require a documented OPSEC review by a TYAD certified OPSEC Level II reviewer. Coordinate all press releases through the COR and TYADs Public Affairs Office.

- Reporting Requirements: Immediately report any attempts by unauthorized third parties to solicit sensitive information to the TYAD Security Operations Branch, the contract POC, and the contractor's Facility Security Officer (FSO).

- Credential Control: Conceal or remove all government-issued badges and identification when off the installation. Do not duplicate, loan, or leave credentials unattended (CACs, badges, and/or parking passes or placards). Report any lost or stolen passes/badges/credentials to TYAD Law Enforcement Branch. The COR will provide all POC contact information.

- Protection of Sensitive Data: Mark and protect internal company data related to this contract (e.g., schedules, deliverables, vulnerability reports) as CUI. All government-provided information, such as drawings and technical data, must be protected in accordance with DoD, Army guidance and guidance within contract package documents.

- Information Disposal: At contract completion or upon Government request, return all government information to the COR or destroy it in accordance with approved TYAD procedures for handling CUI.

- Photography or Videography. Contractors and subcontractors who take photos or video at TYAD must notify their COR at least fourteen business (14) days in advance and complete OPSEC Level I Initial training.  The COR will provide the contractor with the security branch’s points of contact after the contract is awarded.  All individuals must follow TYAD policy regarding photography/videography and the use of personal electronic devices.

All photos and videos must undergo an OPSEC Review—per AR 530-1 Chapter 4—to evaluate them against TYAD’s Critical Information List and identify any vulnerabilities. That review must be fully documented and signed off by a TYAD employee who holds OPSEC Level II certification before disseminated.

COMMUNICATIONS SECURITY (COMSEC) All telephonic and electronic communications with DoD organizations are subject to Communications Security (COMSEC) review and monitoring. The contractor is advised that any calls placed to or received from a DoD organization may be subject to monitoring and recording. The contractor shall ensure frequent dissemination of this notice to all employees who communicate with DoD personnel.

- Information Security (INFOSEC). The contractor shall comply with all applicable regulations for the protection of government information. Information handled under this contract is categorized as either Controlled Unclassified Information (CUI) or Classified National Security Information (CNSI).

Controlled Unclassified Information (CUI) The handling, marking, safeguarding, and destruction of all CUI shall be in strict accordance with DoD Instruction 5200.48, Controlled Unclassified Information (CUI). Specific contractor responsibilities are detailed in the "Safeguarding CUI" section of this document.

- CUI Training Requirement Any contractor or subcontractor personnel who will generate or have access to CUI under this contract must complete mandatory CUI training prior to accessing such information. The "DoD Mandatory Controlled Unclassified Information (CUI) Training" course available on the DCSA CDSE Security Awareness Hub (https://securityawareness.dcsa.mil/cui/) satisfies this requirement. Completion certificates shall be provided to the COR upon request.

- Contractor Responsibilities for Handling CUI – even if it is their own information that must be controlled (example:  Personal Identifiable Information, etc.).  Contractors are responsible for handling CUI when it is created, collected, or maintained in performance of a government contract.  The contractor shall comply with all CUI requirements outlined in Executive Order 13556 and 32 CFR Part 2002. www.dodcui.mil  The contractor's responsibilities include, but are not limited to:

- Marking: Applying uniform CUI markings to all CUI data and deliverables.

- Access Controls: Restricting CUI access to personnel with a lawful government purpose and validated need-to-know.

- Flow Down: Ensuring all CUI protection requirements are passed down to subcontractors.

- Physical Safeguarding: Implementing appropriate physical controls (e.g., locked storage, controlled-access areas) for all CUI, whether in hard copy or on electronic media.

- Incident Reporting: Reporting any actual or suspected loss or compromise of CUI to the COR immediately.

- Disposition: Returning all CUI to TYAD control or destroying it in accordance with DoD and Army guidelines upon contract completion (Deliverable A.002).

- PHYSICAL SECURITY:

Safeguarding of Government Property The Contractor shall be responsible for safeguarding all government equipment, information, and property provided for Contractor use. At the close of each work period, government facilities, equipment, and materials shall be secured.

Key Control - The Contractor shall establish and implement methods of making sure all keys and key cards issued to the Contractor by the Government are not lost, misplaced, or used by unauthorized personnel.

- No keys issued by the Government shall be duplicated.

- The Contractor shall develop a key control procedure, to be included in their Quality Control Plan, which includes procedures for the turn-in of keys by personnel who no longer require access.

- The Contractor shall immediately report any lost or duplicated keys to the Contracting Officer (KO). In the event a key is lost or duplicated, the Government may, at its option, re-key or replace the affected locks, and the total cost shall be deducted from the monthly payment due to the Contractor.

Lock Combinations  The Contractor shall establish and implement methods to ensure that lock combinations are not revealed to unauthorized personnel when applicable. The Contractor shall ensure combinations are changed when personnel with knowledge of the combination no longer have a need-to-know.

1.7  Key Control:  RESERVED.  See Security Requirements section.

1.8  Post Award Conference/Periodic Progress Meetings: The Contractor shall attend any post award conference convened by the contracting activity or contract administration office in accordance with Revolutionary FAR Overhaul FAR Subpart 4.3.  The Contracting Officer, COR, and other Government personnel, as appropriate, may meet periodically with the Contractor to review the Contractor's performance.  At these meetings the Contracting Officer will apprise the Contractor of how the Government views the Contractor's performance and the Contractor shall apprise the Government of problems, if any, being experienced.  Appropriate action shall be taken to resolve outstanding issues.  These meetings shall be at no additional cost to the Government.

1.8.1  The Contractor shall attend, participate in, and furnish input to scheduled and unscheduled meetings, conferences, and briefings that relate to the functions and services herein as required by the Government to provide effective communication and impart necessary information.  The Contract Manager or designated representative shall attend meetings as requested by the Government.  Meeting attendees shall at times include Contractor managerial, supervisory, and other personnel knowledgeable of the subject matter.  Meetings may start or end outside of regular duty hours.

1.9  Contracting Officer’s Representative (COR):  Refer to Part 2 of this PWS for the definition of a COR.  As determined by the Contracting Officer, a COR will be appointed and identified by letter of designation, a copy of which will be provided to the Contractor by the Contracting Officer.  The designation letter states the responsibilities and limitations of the COR, especially with regard to changes in cost or price, estimates, or changes in delivery dates.  The COR is not authorized to change any of the terms and conditions of the resulting order.  The COR monitors all technical aspects of the contract and assists in contract administration.  The COR is not authorized to obligate the Government. If the work is not written in the contract, the COR is not authorized to request new work.  The COR is authorized to perform the following functions:  assure that the Contractor performs the technical requirements of the contract, perform inspections necessary in connection with contract performance, maintain written and oral communications with the Contractor concerning technical aspects of the contract, issue written interpretations of technical requirements, including Government drawings, designs, specifications, monitor Contractor's performance and notifies both the Contracting Officer and Contractor of any deficiencies, coordinate availability of Government property, and coordinate site entry of Contractor personnel.

1.10  Key Personnel:  The following personnel are considered key personnel by the Government:  Contractor’s  Program/Contract Manager and Alternate Program/Contract Manager.  The Contractor shall provide a Program/Contract Manager who shall be responsible for the performance of the work.  The name of this person and an Alternate Program/Contract Manager, who shall act for the Contractor when the Program/Contract Manager is absent, along with a Curriculum Vitae (CV) for each of these individuals, shall be provided in writing to the Contracting Officer no later than during the post award meeting (Deliverable A.003).  (Acceptance of the CV by the Contracting Officer is required before these individuals are permitted to perform any task on this contract.)  The Contract Manager and Alternate Contract Manager shall have full authority to act for the Contractor on all contract matters relating to daily operation of this contract.  The Contract Manager or Alternate Contract Manager shall be available between the applicable hours and days. that have been identified in paragraph 1.5.4. Qualifications for all key personnel are listed below:

a.  Contract Manager and Alternate Contract Manager:  The CV provided by the Contract Manager and Alternate Contract Manager must demonstrate must demonstrate a minimum of 5 years’ experience within the past 10, working as a Program Manager.

b.  Quality Control Manager:  RESERVED

c.  Systems Administrator:  RESERVED

d.  Special Qualifications:  RESERVED

1.11  Identification of Contractor Employees:  All Contractor personnel attending meetings, answering Government telephones, and working in other situations where their Contractor status is not obvious to third parties must identify themselves, to include proper marking of signature blocks in correspondence, to avoid creating an impression in the minds of members of the public that they are Government officials.  The Contractor shall ensure that all documents or reports, produced by Contractors are suitably marked as Contractor products or that Contractor participation is appropriately disclosed.

1.12  Contractor Workspace and Identification:

1.12.1  Contractor workspace (staging site, on-site office, desk or work area, etc.) shall contain a sign signifying the space is occupied by Contractor employee(s) to ensure that Government employees and the public know that they are not Government employees.  The proposed sign shall be submitted to the Contracting Officer via the COR for review and acceptance 10 calendar days after contract award (Deliverable A.004).  Workspace sign location shall be coordinated with the COR.  Contractor employees shall identify themselves by name and company affiliation when answering the telephone, presenting briefings, conducting or attending meetings, and seminars.  All Contractor correspondence (written, facsimile, and email display) shall include their company name.  Requirements for Contractor vehicles is addressed under Part 4 paragraph 4.4.

1.12.2  Contractor Identification Badges:  Contractor personnel shall be easily identifiable through the display of badges IAW Contractor Identification (AE Reg. 27-715).  (For services at Child, Youth, and School Services where children are present, recommend personnel wear identification when children are present.)  The Contractor (to include subcontractors) shall provide each of their employees an easily readable identification badge.  The badge must include the employee’s name, the contractor’s company name, the functional area of assignment, and a recent color photograph of the employee.  Companies with U.S. Government contracts will require their employees to wear these badges visibly when performing work at Government workplaces unless this would be impractical because of mission or safety considerations.  The Contractor shall collect all ID Badges upon completion of the contract or termination of employee.  A listing of issued ID cards shall be furnished to the Contracting Officer prior to the contract performance date and updated as needed to reflect Contractor personnel changes (Deliverable A.005).

1.13  Contractor Travel:  RESERVED

1.14  Other Direct Costs (ODCs):  This category includes travel (outlined in 1.13), printing and shipping expenses associated with training activities and visits to Contractor facilities.  Inclusion of ODCs in this PWS must be preapproved by the Contracting Officer.

1.15  Data Rights:  The Government has unlimited rights to all documents and materials produced under this contract.  All documents and materials, to include the source codes of software, produced under this contract shall be Government owned and are the property of the Government with all rights and privileges of ownership and copyright belonging exclusively to the Government.  These documents and materials may not be used or sold by the Contractor without written permission from the Contracting Officer.  All materials supplied to the Government shall be the sole property of the Government and may not be used for any other purpose.  This right does not abrogate any other Government rights.

1.16  Non-Disclosure Requirements:  Performance under this contract may require the Contractor to access data and information proprietary to a Government agency, another Government Contractor, or of such nature that its dissemination or use other than as specified in this work statement would be adverse to the interests of the Government or others.  The Contractor and Contractor personnel, shall not divulge or release data or information developed, or obtained under performance of this PWS, except to authorized Government personnel or upon written approval of the Contracting Officer.  The Contractor shall not use, disclose, or reproduce proprietary data, which bears a restrictive legend, other than as specified in this PWS.  All documentation showing individual names or other personal information shall be controlled and protected under the provisions of the Privacy Act of 1974, Public Law 93-579, 5 United States Code (U.S.C.) Section 552a.

1.17  Protection of Government and Contract Information:  Per Public Use Notice of Limitations stated by Defense imagery Management operations Center and contained at  https://www.dma.mil/Services/Visual-Information/, the Contractor shall not cite any information (e.g., contract information, pictures, locations, etc.) obtained through this contract on any hard copy or digital marketing tools to include its company website.

1.18  Non-Disclosure Statements:  The Contractor shall provide signed non-disclosure agreements to the Government no later than 10 days prior to commencement of work under the contract (Deliverable A.006).  Disclosure of information by Contractor personnel may result in removal of Contractor personnel from performance under this contract.

1.19  Organizational Conflict of Interest (OCI):  Contractor and subcontractor personnel performing work under this contract may receive, have access to or participate in the development of proprietary or source selection information (e.g., cost or pricing information, budget information or analyses, specifications or work statements, etc.) or perform evaluation services which may create a current or subsequent OCI as defined in Revolutionary FAR Overhaul (RFO) Subpart 9.5.  The Contractor shall notify the Contracting Officer immediately whenever it becomes aware that such access or participation may result in any actual or potential OCI and shall promptly submit a plan to the Contracting Officer to avoid or mitigate any such OCI (Deliverable A.007).  The Contractor’s OCI Mitigation Plan will be determined to be acceptable solely at the discretion of the Contracting Officer.  In the event the Contracting Officer unilaterally determines that any such OCI cannot be satisfactorily avoided or mitigated, the Contracting Officer may affect other remedies as he or she deems necessary, including prohibiting the Contractor from participation in subsequent contracted requirements which may be affected by the OCI.

1.20  Phase In /Phase Out Period:  RESERVED

1.21  Safety:  The following provides information pertaining to Safety and Accident Prevention:

1.21.1  Safety Laws and Regulations:  The Contractor shall comply with Revolutionary FAR Overhaul (RFO) 52.236-13, Accident Prevention (JAN 2026), and the references contained therein (e.g. U.S. Army Corps of Engineers Safety and Health Requirements Manual (EM 385-1-1)).

The requirements under Revolutionary FAR Overhaul (RFO) 52.236-13 and specifically of the EM 385-1-1 include, but are not limited to the following:

(a) Before initiation of work at the job site, an Accident Prevention Plan, written by the Contractor for the specific work and hazards of the contract and implementing in detail the pertinent requirements of EM 385-1-1; will be reviewed for acceptance by designated Government personnel (Deliverable A.008).  Specific requirements for development of the Accident Prevention Plan are found in 01.A and Appendix A of EM 385-1-1. EM 385-1-1 is available online at www.usace.army.mil.

(b) Before beginning each activity involving a type of work presenting hazards not experienced in previous project operations or where a new work crew or subcontractor is to perform work, activity hazard analysis (AHA) shall be prepared by the Contractor performing the work activity (See paragraph 01.a.09 of EM 385-1-1);

(c) The Contractor shall require subcontractors to submit their plan of operations showing methods they propose to use in accomplishing major phases of work;

(d) The Contractor shall discuss the plans in conferences convened by the Contracting Officer prior to starting work on each major phase of operation.  Plans shall include all pertinent information such as layout of haul roads, access roads, storage areas, electrical distribution lines, methods of providing minimum exposure to overhead loads, and methods of access to work areas.  The plan for accomplishing the initial work phase shall be submitted within fifteen (15) calendar days after award of the contract.  Plans for subsequent major phases of work shall be submitted no later than fifteen (15) calendar days prior to initiation of work on each major phase; and

(e) In all areas where construction, demolition, alteration, building, or similar related activities take place, the Contractor shall have the following minimum personal protective clothing and equipment requirements in place for any person working on or visiting the site:

(i) Short sleeve shirt;

(ii) Long trousers;

(iii) Steel-toed safety boots; and

(iv) Hard hat.

1.21.1.1  In addition to other requirements for accident prevention specified in this contract, the Contractor shall comply with all Federal and State requirements governing safety and health protection on construction sites and other applicable occupational safety codes.

The Contractor shall indicate its plan for compliance considering conditions of the work described by the design, technical proposal, operational activities of the Government or others in the area of the work, identification of the coordinator, and implementation of all other accident prevention provisions of this contract. The Contractor shall comply with the non-exclusive list of duties described in this paragraph.  If the Contractor determines that additional activities are required to fully comply, the Contractor shall ensure that compliance with the laws is complete.  The duties include:

(a) Conditions of construction and operational activities to be considered include but are not limited to:

(i) For all construction activities meeting the following criteria:  the work is scheduled to last longer than 30 working days and more than 20 workers are occupied simultaneously, or the volume of work is scheduled to exceed 500 person days, or the work presents particular tasks, e.g. excavations deeper than 5 meters, falls from a height of greater than 7 meters, exposures to hazardous chemical or biological substances, work at less than 5 meters from high voltage lines, underground earth works or tunnels, danger of drowning, diving, use of compressed air, work with ionizing radiation, explosives, or work involving assembly or dismantling of heavy prefabricated components (10 tons or greater).

1.21.1.2  The Contractor shall complete and provide safety notifications required and will provide documented proof to the Contracting Officer via the COR, no later than 10 days that such notifications were made (Deliverable A.009).

SERVICE or EQUIPMENT INSTALLATION CONTRACTOR SAFETY STANDARDS FOR TYAD (June 2024)

Below are some “installation specific” safety standards which contractors are required to adhere to while performing any work on Tobyhanna Army Depot. It is the contractor’s responsibility to always incorporate these particular requirements into their daily operations while under contract and to institute these specifics into their overall site safety controls. These do not substitute or deflect in any way the requirement to institute and adhere to all OSHA 29 CFR 1910 & 1926 and USACE EM385-1 safety standards, as well as all applicable contractual Federal Acquisition Regulations while performing the work under this contract on Tobyhanna Army Depot.

It is the responsibility of the contractor to enforce the below requirements as well as all current revisions of the above referenced standards. Failure to enforce safety requirements on the depot can result in immediate stop works, safety stand down orders and even complete termination of the contract.

Important Phone Numbers:

Fire or Emergency: 911

Fire Department – (Non-Emergency): 570-615-7300

Security: 570-615-7550

Safety Office - 570-615-7027

# S1.0  THE CONTRACTOR IS SOLELY RESPONSIBLE AND LIABLE FOR JOB- SITE SAFETY

- Review of the project plans and other documents by any government appointed official does not constitute an acceptance of Federal responsibility or liability for the adequacy of the safety measures identified for the job or for the Contractor's compliance with all applicable safety rules and regulations.

- The Contractor remains solely responsible and liable for job-site safety at all times during the term of the contract. No outside personnel (other than ET, COR, TYAD Safety, or other government appointed contract personnel) are allowed onto the job site at any time during contract without prior permissions and/or escort by the ET, COR or KO.

- Tobyhanna Army depot has restrictions on the use of fossil fuels in all buildings. When it is determined that electric or other alternatively fueled vehicles are insufficient or unavailable for movement of material within the buildings on the installation, fossil-fueled vehicles can be used only when all alternatives of accepted electric material movement equipment have been considered, and the last option is use of a fossil fuel vehicle or project failure. This includes any situations where safety of employees and equipment may be jeopardized. Convenience will never be an acceptable justification to utilize fossil-fueled vehicles. The Government Designated Representative (GDR) will notify the appropriate supervisor(s) or leader(s) in the area where the need to utilize a fossil fuel vehicle is required. The supervisor / leader will take the necessary steps to notify the employees in the work area of the option to leave the area during the material movement process. The GDR and Contractor will also document all actions the Contractor took to utilize electric or other alternatively fueled vehicles. The documentation will specifically state why electric or alternatively fueled vehicles are insufficient and all mitigation efforts used to minimize the effects of fossil-fueled vehicles to include information as to any appropriate scrubbers that can be utilized along with any ventilation or exhaust systems that can be used to externally vented to the outside of the facility. The documentation must be submitted to the TYAD Safety office for approval prior to any equipment being used.  A final copy of the Approved documentation will be provided to the TYAD Safety Division.

- All direct construction supervision, including subcontractors, must as a minimum, complete an OSHA 30-hour safety course for construction. These certificates must be submitted as part of the site safety plan BEFORE construction activities start (Deliverable A.010).

- RED CARD PROGRAM - Tobyhanna Army Depot utilizes a program to allow employees to stop an action which is considered unsafe. Employees carry small red cards that can be thrown down when employee sees any action they consider unsafe.  Work ceases until TYAD management can decide if it is safe or not. Contractors are required to comply with this program. If a TYAD employee presents the red card to the contractor, the contractor must stop working until the COR and Safety Office can determine if there is a safety hazard or not.

- All contractor personnel, to include subcontractors, vendors, suppliers, or visitors, when performing any type of work activity, or gaining access through an occupied area or shop - must have all applicable personal protective equipment (PPE) that is required for the area to include, but not limited to, hardhats, safety glasses, hearing protection, and respirator protection. Notify both COR & Area Supervision, for access approval and prior to any work activities being performed.

# S2.0  CODE COMPLIANCE

As noted in Tobyhanna Army Depot Safety Regulation 385-1, TYAD follows all requirements and is certified as an ISO 45001 facility. Accordingly, the contractor shall comply with and maintain these high safety   standards and provide full compliance with all applicable safety regulations and standards. The Contractor shall maintain, monitor, and enforce employee compliance         with all applicable rules, regulations, and codes.

Tobyhanna Army Depot requires full contractor compliance with all safety regulations and standards. The Contractor is responsible for maintaining, monitoring, and enforcing all rules, regulations, and codes, by ALL personnel working for the contractor including all subcontractors. These codes include:

Title 29 Code of Federal Regulations-1910 (OSHA General Industry Standards)

Title 29 Code of Federal Regulations-1926 (Construction Industry Standards)

National Fire Protection Association Codes

Uniform Facilities Code

Unified Facilities Guide Specifications (UFGS)

USACE EM385-1-1

All other codes as required to maintain safety standards.

# S3.0  JOB HAZARD ANALYSIS (JHA) / ACTIVITY HAZARD ANALYSIS (AHA)

Prior to the start of work, the contractor shall prepare a JHA / AHA for each phase of work that will be done under the contract. This will be completed in accordance with all applicable OSHA safety requirements. A phase is any operations involving a certain type of work. Examples include demolition, excavation, masonry work, concrete pouring, roofing, and electrical wiring. Work done by each subcontractor is also a phase. The JHA / AHA will:

1. List the activity being performed and identify the sequence of work steps.

2. List the hazards associated with each step, and the procedures and training required to eliminate or reduce the risk to an acceptable level.

# S4.0  SITE SPECIFIC SAFETY & ACCIDENT PREVENTION PLANS

Contractors will submit a written Site-Specific Safety / Contractor Accident Prevention Plan prior to beginning activities (Deliverable A.011). The plan must follow the guidelines in OSHA 29 CFR 1926 or 1910 as applicable.

1. Who will implement the plan, including who is responsible for safety and accident prevention?

2. A means for coordinating and controlling subcontractors and suppliers.

3. Safety training.

4. Who will investigate accidents?

5. Emergency response.

6. Job site cleanup and safe access.

7. Public safety requirements such as signs and barricades.

# S5.0  FALL PROTECTION

1. Personnel performing works at a height of six feet or more from any lower level shall comply with OSHA 29 CFR 1926.500 through 1926.503 safety standards for any type of new installations.  OSHA 29 CFR 1910-28 shall apply to any type of servicing on previously installed equipment.

2. There are currently no certified anchorage points or permanent guardrail systems on any TYAD roof. Most roofs of the depot are more than 20 feet high.

3. Contractors and their employees must be protected from falling off the edge of the roof, regardless of how briefly the employees are at the edge of the roof.

# S6.0  ELECTRICAL SAFETY

Follow the current Tobyhanna Army Depot standard. This standard is based on NFPA 70E.

Copies of the TYAD Electrical standard may be obtained by request from the ET, COR or KO on the project or service contract.

# S7.0  DEPOT REQUIRED PERMITS / APPROVALS

Permits are required for:

1. Excavation: Contractors must utilize the PA 1 Call system and also coordinate with contracting officer representative (COR) for a TYAD dig permit for any excavations prior to any groundbreaking including digging, drilling and stake driving.

2. Trenching: Contractors will adhere to OSHA requirements and receive approval from TYAD Safety office before any trenching deeper than 5 feet is performed. Notifications of such activities will be provided to the COR along with required plans, requests and permits prior to any trenching works being performed (Deliverable A.012). Contractor is responsible for field verifying all utilities and underground entities. Excavation or trench greater than 18 inches in depth that remains open greater than (1) day OR left unattended for any period of time shall have a safety orange construction fence installed around the perimeter of the opening. Caution tape or cones for this purpose is unacceptable.

3. Confined Space: All confined space works on TYAD are to be considered as permit required entries, (unless reclassified by the TYAD Safety office,) and Contractor must first request and be provided with an approved "signed" permit from TYAD Safety Office prior to any confined space entry.  Contractor will refer to all OSHA requirements and must have a confined space plan and all appropriate safety equipment. Contractor is to request approval from TYAD Safety office through COR prior to entry.

4. Burning / fire: Hot work permits must be obtained daily from the Fire Department.

5. Cranes: For use of cranes and all WHE and LHE at TYAD see S.10.13

6. Army Radiation Permits: Non-Army agencies (including other military Services, vendors, and civilian contractors) require an Army Radiation Permit (ARP) to use, store, or possess ionizing radiation sources on TYAD (see 32 CFR 655). Non-Army applicants will apply by letter with supporting documentation to the Depot Commander. The letter should be submitted so that the Depot Commander receives the application at least 30   days before the requested start date of the permit. The ARP application will specify start and stop dates for the ARP and describe the intended use of the radioactive material.

For sealed sources of radiation, i.e. Moisture Soil Density Gauges, the application must include a valid Nuclear Regulatory Commission (NRC) Radioactive Materials License that allows the applicant to use the source as specified in the ARP application, current leak test certificates, operator training records and calibration certificates for any equipment that may be utilized at TYAD.

For machine produced ionizing radiation sources, i.e. X-ray Equipment, the application must include the appropriate state authorization that allows the applicant to use the source as specified in the ARP application along with operator training records and calibration certificates for any equipment that may be utilized at TYAD.

ARPs will not be issued for more than 12 months at a time.

# S8.0  CONFINED SPACES

- All Confined Spaces at TYAD are considered as Permit-Required Confined Spaces unless reclassified by TYAD Safety office after a thorough review of the area and the work being planned.

- Contractors must first notify the COR and receive TYAD Safety office approvals prior to gaining access or opening any confined space area.

- Contractors must fully comply with all OSHA regulations for Confined Space Operations, including on-site use and availability of a Confined Space Entry Permit / Checklists, along with prior approvals of their Accident Prevention Plan and associated Activity Hazard Analysis (AHAs) for the work to be performed.

- The contractor and/or the COR will then notify the TYAD Safety office and TYAD Fire and Emergency Services of the Confined Space Entry timelines and schedules.

5    Upon completion, the contractor will notify the TYAD Safety Office and discuss whether any new hazards were added to the Confined Space and will submit the completed Confined Space Entry Permit / Checklist for record.

S9.0  LOCKOUT/TAGOUT PROCEDURE

1. The Contractor shall perform this work in accordance with 29 CFR § 910.147-The Control of Hazardous Energy requirements.

2. The Contractor shall notify the COR that a lockout/tag out system is going to be used.

3. The contractor is to request the COR to notify them if TYAD is using any lockouts / tag outs in the construction area.

4. The Contractor shall locate and identify all isolating devices.

5. The Contractor shall shut down the equipment normally.

6. The Contractor shall isolate all energy using appropriate methodology.

7. After all work is complete, the Contractor shall remove the energy isolating device and restore the equipment to service.

8. The Contractor shall notify the COR that energy is again restored.

# S10.0 PROTECTION TO THE DRINKING WATER SYSTEM

1. The contractor will not perform any work on the depot potable water system until prior approval is obtained from the Environmental Branch and the certified operator through the Directorate of Installation Services COR.

# S11.0  PROTECTION OF PERSONNEL

At no time is any depot employee to be put at risk to illness or injury. No construction actions are exempt from this requirement.

1. Where pedestrian and driver safety is endangered, use appropriate traffic barricades. Use anchor barricades to prevent displacement by wind. Institute PA DOT regulations and OSHA requirements. Notify the COR prior to beginning such work.

2. Where demolition is required, a Demolition Plan describing the steps and individual Definable Features of Works (DFOWs) as well as safety protocols, controls and oversight is required to be submitted to the COR for review prior to works being performed. Continuously evaluate the condition of the structure being demolished and take action to protect personnel working around the project site. No structural element will be left standing without sufficient support to prevent collapse.

3. Contractor shall provide PPE and provide training for use, for all visitors requiring entry into the regulated area.

4. Subcontractors, vendors, and delivery personnel are the responsibility of the prime contract and must follow the same regulations the prime contractor does.

# S12.0  FIRE AND EMERGENCY SERVICES

Hot Work Permits will be issued by Fire Department upon request. All requests must be made at least thirty (30) minutes prior to the expected start time by contracting the fire department.

1. Contractors are required to have fully charged and operable contractor provided fire extinguishers, in quantities and properly spaced per OSHA requirements that are appropriate for the type of possible fire.  Fire extinguisher shall be immediately available for inspection by the fire department upon an inspection of the worksite and shall remain at the work site at all times. At a minimum, 10 pound class 4A, 60B or C multi-purpose dry chemical fire extinguisher or equivalent shall be provided.

2. A fire watch must be in place during the hot work and for 30 minutes after the HWP operation. Upon completion of the thirty (30) minute, post hot work fire watch, the contractor shall contact the fire department to report the work is complete.

3. Use of a plasma torch will require special approval by the fire department.

4. Any fire, even one that is extinguished, must be reported to the fire department.

5. Ambulance services are provided at a cost to contractors. The contracted ambulance service provider will transport to the nearest hospital. Advanced Life Support, helicopter transport, etc. is all at the contractor's expense.

6. The fire department will respond to all fire, ambulance, hazmat and confined space incidents.

# S13.0  IF AN INCIDENT HAPPENS

1. Any serious injury or medical emergency:

- Immediately call emergency responders

- Dial 911 and give accurate location and nature of emergency. Make sure to tell the operator that you are calling from Tobyhanna Army Depot.

- Send someone to the nearest exit to assist responders.

- Treat victims to the best of your ability.

- Notify COR / call work order desk at 570-615-7805 if there is any blood or body fluids that must be cleaned up.

2. In the event of the smell of natural gas:

- Call dial 911and give accurate location and nature of emergency. Make sure to tell the operator that you are calling from Tobyhanna Army Depot.

- Have all personnel evacuate the area if the smell is significant.

- Upon arrival of fire personnel, provide information as to specific equipment and exact location of potential leak.

3. In the case of a fire:

- If the fire is small, use a fire extinguisher and call 911.

- Otherwise, dial 911 and pull the fire alarm.

- Evacuate the building.

4. Accident/Injury Reports and OSHA 301 Reports:

The contractor shall report to the COR and KO, - Immediately but no later than eight (8) hours, any Fatality, In-patient hospitalization, Amputation, Eye loss or Property damage over $600,000. Similarly, contractor shall report to the COR and KO, – Immediately, but no later than twenty-four (24) hours, all other accidents or near misses.

Notifications shall be followed up within five (5) working days of all incidents (reportable or not) with an OSHA 301 report including all available facts relating to each instance of personal injuries and of loss / damage to Government property.

For any accident that results in illness or injury that requires more than first aid treatment, TYAD Safety & Health Office has the option to have the contractor immediately secure the accident area until released by the accident investigation authority as designated by the Commander.  If the                Government elects to conduct an investigation of the accident, the contractor shall cooperate fully and assist authorities until the investigation is complete.  If requested after the investigation is completed, the contractor shall provide a Corrective Action Plan related to the incident to the COR & KO.

COR to provide copies of all OSHA 301 incident reports and any Correction Action Plans to the TYAD Safety office when available.

# S14.0  CRANE LIFT OPERATIONS AT TOBYHANNA ARMY DEPOT

A Lift Plan for Crane Operations will be submitted to the ET/COR for approval by the TYAD Safety Office at least 14 days prior to a lift operation.  It will conform to all applicable OSHA regulations and requirements and shall include:

1. A description of the operation to be performed, specific personnel assignments (Lift Director, Safety Coordinator, Operator, rigger, etc.) and signaling and any other details pertaining to activities during the lift.

2. A drawn Site Plan with specifications including work zone, support equipment locations, evacuation area, traffic control, electrical power line clearances (if applicable), lift path, surface conditions at crane location, etc.

3. Training/Certifications (scans) for crane operator and other lift-team members included in the lift operation.

4. Equipment nomenclature and a certificate of comprehensive annual inspection records, including any deficiencies and corrective action.

5. Load chart for crane, with target capacities specific to the crane/boom configuration and lift details clearly marked.

6. Lift calculations, including rigging components and configuration.

7. Weather conditions are always part of the ongoing safety assessment and may result in rescheduling of the lift.

8. Only approved operators are allowed to operate or move the crane for any reason.

A Production Lift Plan pertains to repetitive lifts within a work project and may be outlined with one lift plan depicting the nomenclature and general capacities of the equipment to be utilized.  Besides the eight items above, the plan will also include how often the crane will be used and how traffic and personnel safety will be handled.  A separate traffic plan will be required for vetting and approval prior to any lifts taking place.

# S15.0  APPLICATION OF ANY ODOR PRODUCING MATERIAL

1. Any application of any paint, epoxy, adhesive or anything else that produces an offensive odor must be coordinated with the COR or POC before starting. This is particularly true of the construction work in a building occupied by Tobyhanna employees.

2. It is highly recommended that this type of work be planned for off hours, weekends, or holidays to avoid shutdowns of operations due to these offensive odors.  Odors during curing times for products shall also be considered.

# S16.0  CONTROL OF RESPIRABLE CRYSTALLINE SILICA

- Contractors are required to follow the OSHA standard 29 CFR 1926.1153 which requires employers to limit worker exposures to respirable crystalline silica and to take steps to protect their workers and TYAD personnel.

- Contractors shall establish and implement a written exposure control plan that identifies tasks that involve exposure and methods used to protect workers, including procedures to restrict access to work areas where high exposures may occur.

- Restrict housekeeping practices that expose workers to silica by utilizing engineering controls such as local exhaust ventilation, using “wet spray” methods when cutting or drilling and providing proper respiratory protection and other PPE as applicable.

S17.0  OPERATION & MAINTENANCE MANUALS

- The Contractor shall provide to the COR a copy of all Operation and Maintenance (O&M) Manuals and Parts Manuals for any equipment provided.

- The O&M Manuals shall contain a complete set of mechanical drawings and diagrams; a complete set of electrical drawings and diagrams including electrical schematics; logic circuitry descriptions; spare parts list; operator and maintenance instructions for operating, testing, and maintaining all system components.

- The O&M Manuals shall contain complete detailed instructions and schedules for system PM.

- The O&M Manuals shall contain a detailed description of the lock-out/tag-out procedures needed to bring the system and individual components to a zero-energy state for maintenance and servicing.

- The O&M data must be consistent with the manufacturer's standard brochures, schematics, printed instructions, general operating procedures, and safety precautions.

IN ANY CONFLICT BETWEEN STANDARDS, THE STRICTER OF THE TWO SHALL APPLY. IF UNSURE CONTACT THE COR / ET VIA PROPER RFI PROTOCOLS FOR VERIFICATION THROUGH THE TYAD SAFETY OFFICE.

1.22  Environmental Compliance:  The following provides information on Environmental Compliance.

1.22.1  Environmental Compliance Plan and Program:

Standard Specifications for Projects Under the

National Environmental Policy Act

in Accordance with 32 CFR 651

Proponent ELTY-ISP-N

(9 Jun 2025)

***Spill Response Procedures 1-2-3*** 1. Stop work 2. Call 911 3. Evacuate Area *********Damaged Asbestos?********* Environmental Questions? Call Environmental Branch (EB) at 570-615-7098

1.  Air Pollution Control

The contractor must control fugitive emissions, including dust, during the course of their contract.  The contractor must obtain approval from the Environmental Branch (EB) prior to exhausting equipment to the outside.  The contractor must not allow any pollutant or particulate matter to be released to the atmosphere at levels that are visible from outside of Tobyhanna Army Depot (TYAD).  The contractor must not perform work that will release pollutants or particulate matter to the atmosphere when the wind speed exceeds ten miles per hour and will result in adverse effects to the surrounding areas.  TYAD will monitor the wind speed; it is the contractor’s responsibility to obtain wind speed information through the Contracting Officer Representative (COR).

2.  Asbestos

The contractor must ensure that all materials used in the performance of this contract are asbestos-free.

Unless specified in the contract, the contractor must not disturb any existing Asbestos-Containing Material (ACM) in the performance of this contract.  If ACM, or suspect ACM might be disturbed in performance of this contract, the contractor must avoid encountering the material and immediately notify the COR and the Contract Administrator in writing.  The COR must coordinate with EB to have the material tested to determine if there is ACM.  If the material is determined to be ACM and the contractor cannot avoid disturbing the material, the COR will notify the Contracting Officer.  The Contracting Officer will direct a change pursuant to the contract clauses entitled “Changes” and “Differing Site Conditions.”  If ACM, or suspect ACM has been disturbed, the contractor must immediately notify the COR and call the EB.  The contractor will shut down and not move any equipment or supplies near the damaged ACM.  The contractor will evacuate all non-contaminated contractor personnel from the immediate vicinity.  Any contractor personnel thought to be contaminated with asbestos must remain in the area until the EB responds.  If the damaged material is determined to be ACM and there is potential for further damage, the Contracting Officer will direct a change pursuant to the clauses of the contract clauses entitled “Changes” and “Differing Site Conditions.”

Asbestos abatement required under the contract as originally awarded must be in accordance with United Facilities Guide Specification 02 83 14 00 10 and as otherwise required in the contract.  Asbestos abatement not required under the contract as originally awarded, can be incorporated into the existing contract via contract modification, or by the Government taking responsibility for the asbestos abatement.  The method of acquiring the abatement is at the discretion of the Government.  The contractor must have an asbestos abatement work plan that has been approved by EB prior to beginning any asbestos abatement work (Deliverable A.013).

3.  Backflow

The contractor shall have a backflow prevention device installed on all contractor equipment that is connected to TYAD’s water distribution system.  The contractor shall have a water meter installed to monitor water consumption during all phases of the contract. Water use will be reported monthly to the COR.

4.  Burning

The contractor must not burn refuse and debris anywhere on TYAD.

5.  Buy Recycled-Content Materials

The Contractor must comply with Resource Conservation and Recovery Act (RCRA) Section 6002 (42 U.S.C. 6962, Federal Procurement) in the acquisition of materials with recycled content.  Specific designated items in this contract for which recycled content standards have been established have been set forth in the specification (e.g., insulation, roofing materials, carpet, carpet pad, paint, floor tiles, shower and restroom dividers).  Recovered Material Certification: As required by the RCRA, the contractor must certify that the percentage of recovered materials to be used in the performance of the contract will be at least the amount required by the applicable contract specifications Revolutionary FAR Overhaul (RFO) Provision 52.223-4, Recovered Material Certification).  Prior to application for final payment, the contractor must provide a report in accordance with Revolutionary FAR Overhaul (RFO) 52.223-9, Estimate of Percentage of Recovered Material Content for Environmental Protection Agency (EPA) Designated Items, to the Contracting Office.  Compliance with this program does not relieve the contractor from meeting all other specification requirements.

6.  Cultural Resources

The contractor must not adversely affect any property listed on the National Register of Historic Places (NRHP) or properties eligible for inclusion on the NRHP without consultation and approval from the EB through the COR.  If there is a discovery of any historic properties, including archeological sites and graveyards, work will cease immediately until requirements of National Historic Preservation Act, as amended, have been met.  All archaeological artifacts found at TYAD or TYAD-controlled properties are U.S. Government property until a determination is made otherwise.

7.  Demolition Notification

If a project involves the demolition of any load-bearing structural members, whether or not asbestos is present, 25 days prior to the demolition, the Commonwealth of Pennsylvania Asbestos Abatement and Demolition/Renovation Notification Form 2700-FM-BAQ0021 must be submitted to EB as specified in the Unified Facilities Guide Specification 02 82 13.00 10.

8.  Drinking Water

The contractor must not perform any work on the TYAD potable water system prior to obtaining approval from the EB and the Installation Planning and Maintenance Division certified operator through the COR.  If a permit is required due to construction or proposed chemical feed changes, it will be the responsibility of the contractor to obtain all permits associated with the project.  Permit applications will first be reviewed and approved by the Environmental Branch before being submitted to regulatory authorities.  Any piping or additions added to the TYAD water system must be disinfected following “American Water Works Association circular C651-14 "Disinfecting Water Mains."  Construction will be kept outside of drinking water wellhead protection zones when feasible.  All new buildings and remodeled buildings will be equipped with a water meter that can easily be read from the exterior of the building.

9.  Endangered Species

The contractor is responsible for meeting requirements of the Endangered Species Act of 1973.  The contractor must not disturb any endangered species, their habitat or offspring during the implementation of this contract.

10.  Emergency/Spills

All emergencies and spills must be reported to the TYAD Fire Department by calling 911 from a TYAD phone or (570) 615-7300.  If a 911 call is placed on a cell phone, the call will go to the Monroe County Emergency Office.  Notify the Monroe County Emergency Office that you are at TYAD, and the call will be forwarded to TYADs Fire Department.  The contractor must ensure all personnel working on site are trained in the proper procedure according to 29 CFR 1910.120 (if applicable) to initiate a spill response to handle the hazardous substances they are working with.  The contractor will take the necessary actions to prevent and contain spills of hazardous materials.

11.  Energy Resilience and Mission Readiness

The Energy Policy Act of 2005 section 109 and the Energy Independence and Security Act of 2007 require all new construction at federal facilities to be 30% better than ASHRAE 90.1.  Energy Policy Act of 2005 section 104 and the Energy Independence and Security Act of 2007 require all new equipment to be Energy Star qualified when available. This is applicable to heating, ventilation and air conditioning (HVAC) equipment, plumbing, building materials, lighting, commercial food service equipment and appliances.

12.  Environmental Automation and Control Systems

The contractor will not alter, modify, remove or tamper with any environmental automation or control system unless previous arrangement has been made with EB.  This includes sensors, programmable logic controllers, equipment housing, power supplies, meters or other hardware/sensor technology.

13.  Erosion and Sedimentation Control

The contractor shall protect streams, lakes and wetlands from sediment discharges caused by the contractor's activities.  The contractor shall also provide (where applicable) an erosion and sedimentation control plan in compliance with state and local laws and regulations, to the COR for approval prior to executing any soil-disturbing activities.  The contractor must submit a National Pollutant Discharge Elimination System Permit (NPDES) to the Pennsylvania Department of Environmental Protection (PADEP) prior to any construction activity that encompasses more than one acre.  All permits must be reviewed and approved by the EB prior to being sent to any regulatory authority.  The contractor shall not disturb any wetlands.  The contractor is to place silt sock around dirt, rock, or construction debris to ensure runoff does not occur.  The contractor will place silt sock, or drain covers around/in storm drains surrounding the construction and downstream of the site.  Contractor will remove all silt fencing and other temporary control measures once the site is stabilized.  Contractor will remove all spoils from TYAD unless a previously approved disposal site has been established.  The contract COR will be responsible for management and control of the spoil’s disposal site.

14.  Fluorescent and Mercury-Bearing Lamps

The contractor is to collect, containerize, manage and recycle fluorescent and mercury-bearing lamps in accordance with 40 CFR 273, Standards for Universal Waste Management.  A copy of the manifest/Bill of Lading must be given to the EB through the COR five days in advance of shipment by the contractor so that it can be reviewed for accuracy and completeness.  The contractor must install low mercury bulbs when available.

15.  Hazardous Materials Stored and Labeled

The contractor must ensure all hazardous materials (HM) at the work site are properly stored and labeled.  The contractor must not leave any HM behind at the completion of the job for any reason.  HM must not be stored outside without adequate secondary containment and shelter.

16.  Hazardous Waste

The contractor must ensure that all hazardous wastes (HW) at the work site are properly stored and labeled in a pre-approved location designated by the EB.  The contractor must provide copies of any shipping documents for HW/Universal Waste/Toxic Substances Control Act waste.  If the TYAD EPA number is being used for shipping purposes, only EB is authorized to sign a manifest, and the manifest (or copy) must be supplied prior to the day of shipment for review.  The EB will keep original copies.  If HW or waste requiring special handling (e.g., asbestos) is being turned over to the government for disposal, the contactor must notify the EB through the COR when the waste is ready to be moved.

17.  ISO 14001

TYAD is an ISO 14001 certified facility. All contractor and subcontractor employees on site must comply with TYAD Regulation 200-5, “Environmental Management System (EMS).” The contractor may obtain these regulations through the project COR.

18.  Limit of Disturbance

The contractor must confine the limit of disturbance of the project to the smallest area possible.

19.  Mercury-Bearing Equipment

The contractor must not install any equipment, switches, or devices (including thermostats) that contain mercury or lead.

20.  Safety Data Sheets (SDSs)

The contractor must submit SDSs for all hazardous materials proposed for use, including paints, solvents, adhesives, etc., to the EB through the COR five working days prior to material being brought on post.  As of June 1, 2015, all Material Safety Data Sheets (MSDS) must be replaced with new Safety Data Sheets (SDS).  EB will no longer be accepting older legacy MSDS sheets, and the contractor must submit the current SDS for the hazardous material.  The contractor must keep a copy of all SDSs required for the project at the jobsite.

21.  Migratory Bird Protection

The contractor is responsible for meeting requirements of the Migratory Bird Treaty Act of 1918 (as amended).  The contractor must not disturb any migratory bird, their nesting area or offspring during the implementation of this contract.

22.  National Pollutant Discharge Elimination System (NPDES) Permits

The contractor must not perform any work on existing NPDES structures or treatment units unless previously approved in writing by the Installation Planning and Maintenance Division certified operators and the Environmental Branch.  This includes work within the sewage treatment plant, sewage lift stations, sewage conveyance pipes, Industrial Operations Facility pretreatment plant, and storm water sewer systems.  If a permit is required, it will be the responsibility of the contractor to obtain all permits prior to work being performed.  All permit application packages must first be reviewed by the Environmental Branch prior to being sent to any regulatory authority.  All liquids (chemical, cleaner, and lubricants) in containers, drums, and IBC totes are to be stored on secondary containment at all times.  The container shall be labeled with the contents inside and an SDS sheet must be provided to EB.

23.  Net Zero Water

The contractor will minimize the use of potable water during the construction project.  Water used during the construction project will be monitored and measured using portable water meters if possible.  Installed restroom equipment will consist of high-efficiency fixtures that use reduced volumes of water.  Use of flow regulation devices must be approved by EB prior to installation.  Employ strategies that in aggregate use 20% less water than the water use baseline calculated for the building after meeting the Energy Policy Act of 1992 fixture performance requirements.  Automatic hands-free flushometers will not be used.  Water-free urinals will not be used.  Flushometers will be the piston variety that fail in the closed position.  New building construction and renovations will include installation of a water meter that is capable of being read from the outside of the building.

24.  Noise

The contractor must not allow the noise level to exceed 65 decibels at any point outside TYAD property.  If noise levels exceed 65 decibels, a plan must be prepared by the contractor to mitigate the noise levels and submit to the EB for approval through the COR.  The contractor will monitor the fence line to confirm this limit.

25.  Ozone Depleting Substances (ODS)

The contractor must be responsible for ensuring that all personnel who perform maintenance and repair activities on refrigeration equipment have been trained and certified by an EPA-approved Section 608 program.  The contractor must not use Class I or Class II ODS or install equipment that contains Class I or II ODS.  Beginning 1 Jan 26, the contractor must adhere to all AIM Act regulations regarding Hydrofluorocarbon refrigerants, Title 40, Chapter I, Subchapter C, Part 84.

25.  Paints

The contractor must not use paints containing zinc chromate or strontium chromate pigments and paints must not contain a concentration of lead greater than 0.009 percent.  Coatings used within permitted paint spray booths must not have a Volatile Organic Compound (VOC) content greater than 3.50 pounds per gallon.

26.  Pest Management

At no time during the execution of this contract must the contractor provide a food source or harborage for any pests.  The contractor must coordinate through the COR to the EB prior to the application of any pesticide (PA state license is required for pesticide applications).  All pesticides are required to be approved by the EB.  The contractor must report all usage of pesticides the day they are applied through the COR to the EB.  After completion of the contract, the contractor must ensure there is no passage for pests to enter facilities or structures related to work performed by the contractor.

27.  Polychlorinated Biphenyls (PCBs)

The contractor must not bring items containing PCBs onto TYAD.  Light ballasts that are clearly marked "Contains no PCBs," or that are marked with a manufacture date after 1978 must be disposed of by the contractor as construction demolition debris.  Any light ballast that is not marked as containing no PCBs that has a manufacture date prior to 1978, or that cannot be determined whether it contains PCBs, must be disposed of by the contractor at an approved and licensed facility for PCBs.  The contractor must submit a shipping manifest and certificate of disposal of the PCB-containing items to the EB through the COR

28.  Recycling

The contractor must comply with TYADs general recycling plan for recyclable materials such as aluminum, steel, cardboard, paper, plastic and wood.  The contractor should contact the EB for additional information on the recycling of materials through the COR.  The COR will coordinate with EB to have the contractor recycle metals, cardboard, etc., through TYADs recycling program.  All Construction and Demolition (C&D) material transferred from a construction project into the TYAD recycling program must be segregated and material type and weights submitted to the project COR for consolidation.  Any material entering the TYAD recycling program that is not documented and properly reported will be absorbed into the TYAD recycling program and not count towards the C&D requirement of the project.  Clean wood shall be recycled by the contractor off TYAD property.

29.  Refuse and Construction Demolition Debris Removal and Disposal

During the performance of all construction, renovation and demolition projects, a minimum of 60 percent of all non-hazardous construction demolition debris shall be diverted from the landfill for reuse or recycling.  The contractor shall provide written certification to the COR of the type and tonnage of debris reused or recycled from the contract.  All refuse and the construction demolition debris not recovered for reuse or recycling shall be disposed of at a PADEP permitted and Monroe County Municipal Waste Management Authority authorized facility.  The contractor shall comply with the Monroe County Solid Waste Management Plan, PA Act 90, and all applicable licensing requirements.  All waste must be transported to designated Monroe County landfills; see http://www.thewasteauthority.com for details.  For questions, contact the Monroe County Municipal Waste Management Authority at (570) 643-6100.  The contractor shall provide a disposal certificate or landfill weight slip to the COR for all solid waste disposed of during the performance of this contract.  The COR will then provide copies of the disposal certificate or landfill weight slips with the quarterly consolidated C&D report from The Installation Planning and Maintenance Division to EB.

30.  Removal Materials

The contractor must remove from the site prior to the acceptance of work by the Government, all materials not identified to remain in place, including excess paints, building materials and equipment purchased by the contractor for the execution of this project.

31.  Site Preservation and Restoration

The contractor must ensure that the land resources associated under this contract be preserved in their present condition or be restored to a like condition after completion of construction.  This post construction appearance will appear to be natural and not detract from the appearance of the project.

32.  Trees and Shrubs Protection

The contractor must be responsible for the protection of all trees and shrubs on site.  The contractor must not allow any heavy equipment, vehicular traffic or stockpiling of materials within ten feet from the drip line of any tree.  The contractor must not allow any toxic materials to be stored within 100 feet (35.5 meters) of the drip line of any tree.  The contractor must not nail protective devices, signs, utility boxes or other objects to trees to be retained on the site.

33.  Unexploded Ordnance (UXO)

All work that is done in the UXO area must include the support and clearance by a UXO technician.  In addition, all personnel entering the UXO area must have UXO recognition training.  The COR will escort the contractor to the EB for UXO recognition training.  The COR will provide a map of the UXO area to the contractor.

34.  Water Quality

The contractor shall not pollute streams, lakes or reservoirs.  All work under this contract shall be performed in such a manner that pollution will not be created in streams, surface waters or underground water located within, or adjacent to the project area.  The contractor shall not spill, emit, dump or otherwise discharge any hazardous, toxic, harmful or unauthorized pollutant, substance or material, including petroleum products, cleaning agents or paints, onto the ground, into the air or into any waters or nearby storm drain.  The contractor shall execute any preventative measures required to prevent any hazardous, toxic or harmful material stored or used on the project site from entering any stormwater drain.  Nothing shall be allowed to spill, emit, dump or otherwise discharge any hazardous, toxic or harmful material or pollutant into any sink, toilet, drain, utility or receptacle without written permission from the EB through the COR.  The contractor shall protect streams, lakes and wetlands from sediment discharges caused by his activities.  The contractor shall contract the EB immediately in the event of a spill.

1.23  Required Training:  RESERVED.  See Security Requirements section.

1.24  Authorization to Perform Services in Germany:  RESERVED

1.25  Notice to Proceed:  The notice to proceed will be provided as indicated below.

☐The effective date of contract will constitute the date of notice to proceed

☒A notice to proceed letter will be issued

☐The date of the letter transmitting the contract will constitute the date of the notice to proceed

1.26  Electromagnetic Compatibility Directive:  RESERVED

1.27  Government Property and Services:  RESERVED

1.28  Conventional Forces Europe (CFE) Treaty Verification Inspection:  RESERVED

1.29  Cybersecurity Maturity Model Certification (CMMC):

CONTRACTOR COMPLIANCE WITH THE CYBERSECURITY MATURITY MODEL CERTIFICATION (CMMC) LEVEL REQUIREMENTS (NOV 2025)

(a) Definitions. As used in this clause-

Controlled unclassified information means information the Government creates or possesses, or information an entity creates or possesses for or on behalf of the Government, that a law, regulation, or Governmentwide policy requires or permits an agency to handle using safeguarding or dissemination controls (32 CFR 2002.4(h)).

Current means—

(1) With regard to Conditional Cybersecurity Maturity Model Certification (CMMC) Status—

(i) Not older than 180 days for Conditional Level 2 (Self) assessments and Conditional Level 2 (certified third-party assessment organization (C3PAO)) assessments, with—

(A) No changes in compliance with the requirements at 32 CFR part 170 since the Conditional CMMC Status date (see 32 CFR 170.16 and 170.17); and

(B) A corresponding affirmation of continuous compliance by an affirming official (see 32 CFR 170.4); and

(ii) Not older than 180 days for Conditional Level 3 (Defense Industrial Base Cybersecurity Assessment Center (DIBCAC)) assessments, with—

(A) No changes in compliance with the requirements at 32 CFR part 170 since the Conditional CMMC Status date (see 32 CFR 170.18); and

(B) A corresponding affirmation of continuous compliance by an affirming official;

(2) With regard to Final CMMC Status—

(i) Not older than 1 year for Final Level 1 (Self), with—

(A) No changes in compliance with the requirements at 32 CFR part 170 since the Final CMMC Status date (see 32 CFR 170.15); and

(B) A corresponding affirmation of continuous compliance, not older than 1 year, by an affirming official;

(ii) Not older than 3 years for Final Level 2 (Self) assessments and Final Level 2 (C3PAO) assessments, with—

(A) No changes in compliance with the requirements at 32 CFR part 170 since the Final CMMC Status date (see 32 CFR 170.16 and 170.17); and

(B) A corresponding affirmation of continuous compliance, not older than 1 year, by an affirming official; and

(iii) Not older than 3 years for Final Level 3 (DIBCAC) assessments, with—

(A) No changes in compliance with the requirements at 32 CFR part 170 since the Final CMMC Status date (see 32 CFR 170.18); and

(B) A corresponding affirmation of continuous compliance, not older than 1 year, by an affirming official; and

(3) With regard to affirmation of continuous compliance (32 CFR 170.22), not older than 1 year with no changes in compliance with the requirements at 32 CFR part 170.

Cybersecurity Maturity Model Certification (CMMC) status means the result of meeting or exceeding the minimum required score for the corresponding assessment. The potential statuses are as follows:

(1) Final Level 1 (Self).

(2) Conditional Level 2 (Self).

(3) Final Level 2 (Self).

(4) Conditional Level 2 (C3PAO).

(5) Final Level 2 (C3PAO).

(6) Conditional Level 3 (DIBCAC).

(7) Final Level 3 (DIBCAC).

Cybersecurity Maturity Model Certification unique identifier (CMMC UID) means 10 alpha-numeric characters assigned to each CMMC assessment and reflected in the Supplier Performance Risk System (SPRS) for each contractor information system.

Federal contract information (FCI) means information, not intended for public release, that is provided by or generated for the Government under a contract to develop or deliver a product or service to the Government. It does not include information provided by the Government to the public, such as on public websites, or simple transactional information, such as information necessary to process payments.

Plan of action and milestones means a document that identifies tasks to be accomplished. It details resources required to accomplish the elements of the plan, any milestones in meeting the tasks, and scheduled completion dates for the milestones, as defined in National Institute of Standards and Technology Special Publication 800-115 (32 CFR 170.21).

(b) Framework. The Cybersecurity Maturity Model Certification (CMMC) is a framework for assessing a contractor's compliance with applicable information security protections (see 32 CFR part 170).

(c) Duplication. The CMMC assessments will not duplicate efforts from any other comparable DoD assessment, except for rare circumstances when a reassessment may be necessary, for example, when there are indications of issues with cybersecurity and/or compliance with CMMC requirements.

(d) Requirements. The Contractor shall—

(1)(i) Have and maintain for the duration of the contract a current CMMC status at the following CMMC level, or higher:  CMMC Level 2 (C3PAO) for all information systems used in performance of the contract, task order, or delivery order that process, store, or transmit FCI or CUI; and

(ii) Consult 32 CFR 170.23 related to the flowdown of the CMMC requirements, and flow down the correct CMMC level to subcontracts and other contractual instruments;

(2) Only process, store, or transmit FCI or CUI on contractor information systems that have a CMMC status at the CMMC level required in paragraph (d)(1) of this clause, or higher;

(3) Complete on an annual basis, and maintain as current, an affirmation, by the affirming official (see 32 CFR 170.4), of continuous compliance with the requirements associated with the CMMC level required in paragraph (d)(1) of this clause in the Supplier Performance Risk System (SPRS) ( https://piee.eb.mil) for each CMMC UID applicable to each of the contractor information systems that process, store, or transmit FCI or CUI and that are used in performance of the contract;

(4) Ensure all subcontractors and suppliers complete prior to subcontract award, and maintain on an annual basis, an affirmation, by the affirming official (see 32 CFR 170.4), of continuous compliance with the requirements associated with the CMMC level required for the subcontract or other contractual instrument for each of the subcontractor information systems that process, store, or transmit FCI or CUI and that are used in performance of the subcontract; and

(5) If the Contractor has a CMMC Status of Conditional, successfully close out a valid plan of action and milestones (32 CFR 170.21) to achieve a CMMC Status of Final.

(e) Reporting. The Contractor shall—

(1) Submit to the Contracting Officer—

(i) The CMMC UID(s) issued by SPRS for contractor information systems that will process, store, or transmit FCI or CUI during performance of the contract (Deliverable A.014); and

(ii) Any changes in the CMMC UIDs generated in SPRS throughout the life of the contract, task order, or delivery order, if applicable (Deliverable A.015);

(2) Enter into SPRS the results of a current self-assessment for each CMMC UID, not covered by a C3PAO assessment or DIBCAC assessment, applicable to each of the contractor information systems that process, store, or transmit FCI or CUI and that are used in performance of the contract; and

(3) Complete in SPRS on an annual basis and maintain as current an affirmation of continuous compliance by the affirming official (see 32 CFR 170.4) for each self-assessment, C3PAO assessment, or DIBCAC assessment required under the contract in SPRS.

(f) Subcontracts. The Contractor shall—

(1) Insert the substance of this clause, including this paragraph (f) and excluding paragraph (e)(1), in subcontracts and other contractual instruments, including those for the acquisition of commercial products and commercial services, excluding commercially available off-the-shelf items, if the subcontract or other contractual instrument will contain a requirement to process, store, or transmit FCI or CUI; and

(2) Prior to awarding a subcontract or other contractual instrument, ensure that the subcontractor has a current CMMC certificate or current CMMC status at the CMMC level that is appropriate for the information that is being flowed down to the subcontractor based on the requirements at 32 CFR 170.23.

(End of CMMC clause)

PART 2

DEFINITIONS & ACRONYMS

2.  Definitions and Acronyms

2.1  Definitions:  Although not inclusive of every term used within this PWS, the following provides a list of definitions used throughout this PWS and commonly used in the acquisition field.

Contracting Officer – means a person with the authority to enter into, administer, and/or terminate contracts and make related determinations and findings on behalf of the Government. Note: The only individual who can legally bind the Government.

Contracting Officer's Representative (COR) – As defined in PGI 201.602-2, means an individual designated and authorized in writing by the Contracting Officer to perform specific technical or administrative functions. DoD Instruction (DoDI) 5000.72, Part II Definitions states the following when defining a COR: “Defined in subpart 202.101 of Reference (f). Any individual delegated responsibilities pursuant to subpart 1.602-2 of Reference (e), regardless of local terminology, must be certified in accordance with this instruction. For example, local terminology can be COR, Contracting Officer’s technical representative, technical point of contact, technical representative, alternate COR, administrative COR, assistant COR, line item manager, task order manager, quality assurance personnel, quality assurance evaluator, or COR management.” In addition, Army Regulation 70-13, Chapter 2, paragraph 2-2g, states, in part, the following when providing other surveillance support personnel to assist the COR when needed, “…These other surveillance support personnel may serve as on-site representatives of the COR in performance of actual contract surveillance if they meet all COR requirements and have been appointed by the Contracting Officer as alternate CORs.”

Contractor – means a supplier or vendor awarded a contract to provide specific supplies or service to the Government. The term used in this contract refers to the prime.

Contractor-acquired Property - means property acquired, fabricated, or otherwise provided by the Contractor for performing a contract and to which the Government has title.

Day – means, unless otherwise specified, a calendar day.

Defective Service – means a service output that does not meet the standard of performance associated with the Performance Work Statement.

Deliverable – means anything that can be physically delivered, but may include non-manufactured things such as meeting minutes or reports.

Government-furnished Property – As reflected in Revolutionary FAR Overhaul (RFO) 52.245-1, Government-furnished Property “means property in the possession of, or directly acquired by, the Government and subsequently furnished to the Contractor for performance of a contract. Government-furnished property includes, but is not limited to, spares and property furnished for repair, maintenance, overhaul, or modification. Government-furnished property also includes contractor-acquired property if the contractor-acquired property is a deliverable under a cost contract when accepted by the Government for continued use under the contract

Government Property - means all property owned or leased by the Government.  Government property includes both Government-furnished and Contractor-acquired property. Government property includes material, equipment, special tooling, special test equipment, and real property. Government property does not include intellectual property and software.

Property Administrator - means an authorized representative of the Contracting Officer appointed in accordance with agency procedures, responsible for administering the contract requirements and obligations relating to Government property in the possession of a Contractor.

High Level Objective (HLO) – means a key overarching result-based objective for a project necessary to achieve the project’s vision. HLOs are similar to Level 2 in a Work Breakdown Structure. Each HLO may contain several statements to flesh out the areas necessary to meet the objective.

Physical Security – means that part of security concerned with physical measures designed to safeguard personnel; to prevent unauthorized access to equipment, installations, material, and documents; and to safeguard against espionage, sabotage, damage, and theft.

Quality Assurance – (or Government contract quality assurance) means the various functions, including, inspection, performed by the Government to determine whether a Contractor has fulfilled the contract obligations pertaining to quality and quantity.

Quality Assurance Surveillance Plan (QASP) – means the key Government-developed surveillance process document, and is applied to Performance-Based Service Contracting (PBSC). The QASP is used for managing Contractor performance assessment by ensuring that systematic quality assurance methods validate that Contractor quality control efforts are timely, effective, and are delivering the results specified in the contract or task order. The QASP directly corresponds to the performance objectives and standards (i.e., quality, quantity, timeliness) specified in the Performance Work Statement (PWS). It provides specific details on how the Government will survey, observe, test, sample, evaluate, and document Contractor performance results to determine if the Contractor has met the required standards for each objective in the PWS. The QASP, with very few if any exceptions, is an internal to Government document.

Quality Control – means all necessary measures taken by the Contractor to assure that the quality of an end product or service shall meet contract requirements.

Statement – means the specific results-based activities required to satisfy HLOs. A statement contains a result, the context of the statement, and the required action(s). Statements focus on “what” is to be accomplished; however they are not prescriptive in describing “how” the outcome is to be achieved. Each HLO may have several statements to flesh out the areas necessary to meet the objective. Statements are similar to Level 3 in a Work Breakdown Structure.

Subcontractor – means one that enters into a contract with a prime Contractor. The Government does not have privity of contract with the subcontractor.

Work Day - The number of hours per day the Contractor provides services in accordance with the contract.

Work Week - Monday through Friday, unless otherwise specified.

2.2  Acronyms:  Although not inclusive of every term used within this PWS, or that may be included in an acquisition, the following provides a list of acronyms commonly used in the acquisition field.

ACOR			Alternate Contracting Officer's Representative

AE 			Army in Europe

AFARS		Army Federal Acquisition Regulation Supplement

AHA			Activity Hazard Analysis

AOR			Area of Responsibility

AR			Army Regulation

AT			Anti-terrorism

ATCTS		Army Training Certification Tracking System

CAC			Common Access Card

CADD			Computer-Aided Design and Drafting

CCE			Contracting Center of Excellence

CFE 			Conventional Forces Europe

CFR			Code of Federal Regulations

CMMC		Cybersecurity Maturity Model Certification

CONUS		Continental United States (excludes Alaska and Hawaii)

COR			Contracting Officer’s Representative

COTS			Commercial-Off-the-Shelf

DA			Department of the Army

dBA			A-weighted decibels

DCP			Dust Collection Port

DD250		Department of Defense Form 250 (Receiving Report)

DD254		Department of Defense Contract Security Requirement List

DFARS		Defense Federal Acquisition Regulation Supplement

DMDC			Defense Manpower Data Center

DoD			Department of Defense

FAR			Federal Acquisition Regulation

FRG			Federal Republic of Germany

GFP			Government Furnished Property

HLO			High Level Objective

HIPAA		Health Insurance Portability and Accountability Act of 1996

IA			Information Awareness

IAC			Installation Access Control

IACO			Installation Access Control Office

ID			Identification

IGCE			Independent Government Cost Estimate

IT			Information Technology

JHA			Job Hazard Analysis

JTR			Joint Travel Regulation

JPAS			Joint Personnel Adjudication System

KO			Contracting Officer

NEC			National Electric Code

NEMA			National Electrical Manufacturers Association

NFPA			National Fire Protection Association

NTP			Notice to Proceed

OCI			Organizational Conflict of Interest

OCONUS		Outside Continental United States (includes Alaska and Hawaii)

ODC 			Other Direct Costs

OPSEC		Operations Security

OSHA			Occupational Safety and Health Administration

PA			Property Administrator

PDHR			Pull Down Hose Reel

PII			Personally Identifiable Information

PIPO			Phase In/Phase Out

PM			Preventive Maintenance

POC			Point of Contact

PPE			Personal Protective Equipment

PRS			Performance Requirements Summary

PWS			Performance Work Statement

QA			Quality Assurance

QAP			Quality Assurance Program

QASP			Quality Assurance Surveillance Plan

QC			Quality Control

QCP			Quality Control Program

RA			Requiring Activity

RCO			Regional Contracting Office

SDS			Safety Data Sheets

SIGE			Safety and Health Protection Plan

TE			Technical Exhibit

TYAD			Tobyhanna Army Depot

UFC			United Facility Criteria

USAG			United States Army Garrison

USAREUR		United States Army Europe
UOM 			Unit of Measure

VOC			Volatile Organic Compound

PART 3

GOVERNMENT PROPERTY (GP) AND SERVICES

3.  Government Property and Services

3.1  Services:  The Government will provide the location for the contractor-supplied refuse receptacle.

3.2  Facilities:  RESERVED

3.3  Utilities:  The Government will furnish electrical, compressed air, and breathable air connectivity up to the exterior connection points on the booth provided by the contractor. Utilities will be furnished by the Government within 30 feet of the work site.

3.4  Equipment:  RESERVED

3.5  Special Tooling and Test Equipment:  RESERVED

3.6  Materials:  Upon request, the Government will provide applicable publications, manuals, regulations, etc. mentioned in the PWS and listed in Part 6.

3.7  Training:  The Government will provide the following training:  AT Level 1 Awareness, OPSEC, iWATCH, and CUI.

3.8  Common Access Cards (CAC):  RESERVED

PART 4

CONTRACTOR FURNISHED ITEMS AND SERVICES

4.  Contractor Furnished Property and Services

4.1  General:  The Contractor shall furnish all materials, supplies, freight, delivery, tools, equipment, consumables, labor, and supervision for the turn-key design, supply, delivery, installation, assembly, set-up, and training to install the new sanding booth and other items necessary to perform services as described in the PWS and associated contract documents, except for those items specified in Part 3 Government Property and Services.

4.2  Secret Facility Clearance:  RESERVED

4.3  Materials:  The Contractor shall provide PPE as outlined previously.  The Contractor shall provide all components of the sanding booth system, including but not limited to the frame, panels, doors, filtration systems, lighting, electrical controls, fire suppression, and all accessories.  The Contractor shall also provide all paints, fluids, greases, lubricants, and associated SDSs.

4.4  Vehicles and Equipment:  The Contractor shall provide all necessary vehicles (no GSA vehicles provided to Contractor for use on this contract) and equipment to perform the work described in this PWS.  Only electric-powered tools and equipment shall be used inside the building.  All Contractor provided vehicles and equipment shall have the company name prominently displayed on both sides of the vehicle or equipment and present a neat, professional appearance.  Contractor's vehicles and equipment used in the performance of this contract shall meet all local traffic, safety, and environmental requirements.  Vehicles and equipment found to be unsafe shall be removed from the installation and replaced.  The Contractor shall not use any Government-owned tools, materials, or parts to maintain Contractor vehicles and equipment without prior written approval of the Contracting Officer. The COR may inspect the Contractor’s vehicles and equipment at any time.

4.5  Background Checks:  Background checks are required for all contractor and subcontractor personnel prior to on-site access at TYAD.  The Contractor shall provide background checks in accordance with this PWS and as determined by the Government.

PART 5

SPECIFIC TASKS

5.1  Basic Services:  The Contractor shall provide all services for the turn-key design, supply, delivery, installation, assembly, set-up, and training for a new crossdraft-style sanding booth at TYAD.

5.2  Tasks:  Tasks consist of the following:

5.2.1  Project Management and Design

5.2.1.1  Post-Award Conference:  The contractor shall attend a post award meeting at TYAD within 15 calendar days of contract award to present an action plan (Deliverable A.016) and timeline.

(a) STD:  Meeting held within 15 calendar days of award.

AQL:  100% Compliance.

5.2.1.2  System Layout Drawings:  The Contractor shall provide a to-scale, full-assembly layout drawing package (Deliverable A.017) for approval before commencing work.

(a) STD:  Drawing package submitted in .dwg and hardcopy format within 45 calendar days of award.  Work shall only begin upon Government approval.

AQL:  100% Compliance.

5.2.2  Sanding Booth Design and Installation

5.2.2.1  Booth Structure and Design:  The contractor shall install a modular, self-supporting, crossdraft-style sanding booth.

(a) STD:  Minimum internal dimensions of 39’L x 16’W x 14’H.  Constructed of 18-gauge steel panels.  Includes front bifold door, rear roll-up door, one regular and one double-wide personnel door.

AQL:  No deviation from specified requirements and materials.

(b) STD:  The sanding booth shall be designed and constructed to meet all applicable Occupational Safety and Health Administration (OSHA), National Fire Protection Association (NFPA), United Facility Criteria (UFC) and Local codes including, but not limited to, OSHA standards for Ventilation, Occupational Noise Exposure, and Air Contaminants to include any and all options available for additional sound proofing for maximum sound reductions.  The booth shall comply with the hazardous location classification system as defined by the National Fire Protection Association (NFPA) 70, National Electric Code (NEC) for NFPA 70 NEC Hazardous Location Class 1, Division 1.  The Contractor is responsible to work with a Fire Protection Engineer to ensure that applicable requirements for the booth are identified and met.

AQL:  No deviation from specified requirements and materials.

(c) STD:  The sanding booth shall follow the current Ventilation Design Criteria standards of the American Conference of Governmental Industrial Hygienists (ACGIH).  All make-up air shall  come from a clean source outside the building(s) in which the system is located.  All air containing dust from any source shall go through the filters and shall be able to be exhausted outside the building.  The outside intake and exhaust shall be constructed to prevent precipitation from entering.  Make-up air inlet(s) shall be situated and located to avoid contamination from any nearby exhaust air sources.  The intake air shall be monitored, at a minimum, for combustible gases, carbon monoxide and carbon dioxide.  All outside air intakes and exhausts shall be screened to prevent the entrance of birds and other small animals.  No loads, except ducts, shall be placed on or supported by the building structure.  All such loads shall be floor supported independent of the building’s structural members.

AQL:  No deviation from specified requirements and materials.

(d) STD:  The booth shall include a carbon monoxide monitor equipped with internal explosion proof audible and visual horn / strobe and external display meter / control panel with status lights for breathable air connections.

AQL:  No deviation from specified requirements and materials.

(e) STD:  The booth shall comply with all applicable OSHA and industry safety standards.  If equipment is not manufactured in the US and shall bear a CE label of European or other similar standard, under OSHA's NRTL requirements, the product must also have the specific mark of one of the OSHA’s NRTLs recognized to test and certify the product.

AQL:  No deviation from specified requirements and materials.

(f) STD:  All sanding booth framework, wall and ceiling panels shall be painted white on both the interior and exterior sides.

AQL:  No deviation from specified requirements and materials.

5.2.2.2  Filtration and Ventilation:  The contractor shall install a four-stage air filtration system.

(a) STD:  System shall include a three-stage or similar type air filtration system, plus a fourth stage for VOC filtration.  [This is NOT a dust collection system.]  The first stage shall consist of roll type media, the second shall be a panel-type filter and the third shall be a bag type filter.  The additional fourth stage shall be a VOC filtration system designed to include HEPA Activated Carbon Filtration.  Alternative equivalent proposals will be considered.  The sanding booth shall employ magnehelic pressure gauges to allow for monitoring of static pressure drop across stages of the filtration system.  Magnehelic pressure gauges must be installed to measure the total differential pressure in inches of water column across the exhaust filters. air filtration system (NOT a dust collection system)

AQL:  100% Compliance.

5.2.2.3  Electrical and Lighting:  The contractor shall install all electrical and lighting systems.

(a) STD:  Interior LED lighting providing 100 foot-candles.  All fixtures, controls, and wiring to meet NFPA 70 NEC Hazardous Location Class 1, Division 1 standards.

AQL:  100% Compliance.

(b) STD:  Based on results of fibrous dust explosivity tests (see attachment 4), TYAD Safety Division requires the system to meet National Electrical Code (NEC) Standard for Class 1, Division 1 Environment.  All electrical controls shall be minimum of a Type 12 National Electrical Manufacturers Association (NEMA) rated.  Control panel shall consist of a UL-508A listed with a single-point connection to main electrical disconnect.

AQL:  100% Compliance.

5.2.2.4  Fire Protection:  The contractor shall install a water-based fire suppression and alarm system.

(a) STD:  System must meet UFC 3-600-01 and NFPA standards and connect to the existing building Notifier fire alarm system. All devices must be Class 1, Division 1 rated.

AQL:  100% Compliance.

(b) STD:  The system shall be designed and constructed with a water-based fire suppression system. The fire suppression system shall meet United Facility Criteria (UFC) 3-600-01 and NFPA standards.  The Contractor is responsible to determine whether the existing water-based fire suppression system has adequate extra capacity for the size of the booth.  The Contractor is responsible for making sure the suppression system can handle an extension for the added supply to the new booth.  If deemed necessary based on the capacity calculations, the Contractor shall be required to increase the pipe size, increase sprinkler K-factor, provide additional sprinklers, etc. to meet the UFC and NFPA standards.  Tobyhanna requires schedule 40 pipe to be used with sprinkler systems.  Tobyhanna requires any new or renovated sprinkler piping to be painted red.

AQL:  100% Compliance.

(c) STD:  The system shall include explosion proof fire alarm visual and audible notification devices suitable for the conditions within the booth.  The sanding booth shall be designed and constructed with fire alarm notification devices that meet UFC and NFPA standards and shall be designed and constructed with fire alarm and alert strobes that meet UFC and NFPA standards.  These devices shall be connected to the existing Notifier fire alarm system.  Fire Alarm Warning devices shall meet the Class 1 Division 1 classification (Horns, Strobes, Smoke / Heat Detectors).

AQL:  100% Compliance.

5.2.2.5  Accessories:  The contractor shall install all specified accessories.

(a) STD:  System shall include two 30' fall protection rails, three compressed air hose reels, a central vacuum system with six ports, six utility niches, and a minimum of four (4) breathable air connections and six (6) compressed air connection points both internally and externally.

AQL:  100% Compliance.

5.2.2.6  Environmental:  The contractor shall meet all environmental requirements.

(a) STD:  The sanding booth is used for fiberglass repair work.  Fiberglass (FIBROUS GLASS DUST 65997-17-3 (Fibrous Glass) is considered a nuisance dust by the Occupational Safety and Health Administration (OSHA) and has an exposure standard (see Table 1 below) which needs to be controlled.  The following shall be utilized:  Enclosing the booth, utilizing HEPA filtered ventilation negative pressure, and utilizing wet methods – all combined to control the hazards while deconstructing the booth.  There are additional controls required, both administrative and PPE requirements to be determined in consultation with TYAD Environmental Branch Asbestos Program Manager, Matthew Argust, X6594.  The contract shall require a certified air technician to monitor the air standards listed below.  Fiberglass waste must be double bagged and goosenecked but can be placed in a regular construction and demolition rolloff.  Environmental Branch must inspect remediations prior to the start of work.  Point of contact is Devin Zurawski on requirements for air permit modification, X5023.

| Table 1 Exposure Standards |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| OSHA PEL 8-hour TWA (ST) STEL (C) Ceiling Peak |  | NIOSH REL Up to 10-hour TWA (ST) STEL (C) Ceiling |  | ACGIH TLV© 8-hour TWA (ST) STEL (C) Ceiling |  | CAL/OSHA PEL 8-hour TWA (ST) STEL (C) Ceiling Peak |  |
| PEL-TWA | OSHA Maritime PEL: 15 mg/m³ as Fibrous Glass, 8 hr TWA. | REL-TWA | 3 fibers/cm³ (fibers ≤3.5 µm in diameter, ≥10 µm in length); 5 mg/m³ (total) | TLV-TWA | 1 fiber/cc (continuous filament glass fibers, glass wool fibers, rock wool fibers, slag wool fibers and special purpose glass fibers, [F]); 5 mg/m³ (continuous filament glass fibers, inhalable particulate matter]); 0.2 f/cc (refractory ceramic fibers [F]) [1999] | PEL-TWA | 1 fiber/cm³ [q] |
| PEL-STEL |  | REL-STEL |  | TLV-STEL |  | PEL-STEL |  |
| PEL-C |  | REL-C |  | TLV-C |  | PEL-C |  |
| Skin notation | N | Skin notation | N | Skin notation | N | Skin notation | N |
| Notes: See 29 CFR 1915.1000 Table Z-Shipyards. For General Industry, please see 29 CFR 1910.1000 Table Z-3, Mineral Dusts for Inert or Nuisance Dust. For Construction, see29 CFR 1926.55 Table 1, for Inert or Nuisance Particles. |  | Notes: |  | Notes: See TLV endnote [F]. |  | Notes: [q] Fibers per cubic centimeter of air at 25°C and 760 mmHg pressure. To be considered a fiber for this limit the glass particle must be longer than 5µm, have a length to diameter ratio of three or more, and have a diameter less than 3µm. The National Institute for Occupational Safety and Health (NIOSH), Method 7400, Issue 2, August 15, 1994, which is hereby incorporated by reference, shall be used for measuring airborne fiber concentrations. |  |

AQL:  100% Compliance.

5.2.2.7  Fire Safety:  The contractor shall acquire necessary permits.

(a) STD:  Prior to soldering, welding, torch cutting, and all forms of burning and use of open flame, the Contractor shall be responsible to obtain a Burn Permit from the TYAD Fire Department.  The Contractor shall use safety screens that offer the required level of protection for the type of work being performed and to provide protection for all personnel in the surrounding area.  Soldering, welding, torch cutting, all forms of burning, require removal of paint prior to operations.  Paint must be removed at a minimum of two inches from where soldering, welding, torch cutting, all forms of burning are performed.  Paint may be sanded or ground.  All sanding/grinding/drilling equipment is required to have dust/fume capture equipment with HEPA vacuum controls.

AQL:  No deviation from specified requirements and materials.

5.2.3  Site Work and Completion

5.2.3.1  Site Preparation:  The Contractor shall perform all site preparation, including saw-cutting the concrete floor using wet methods and HEPA vacuums to control dust.

(a) STD:  In coordination with TYAD COR, any demolition shall be planned for off hours, weekends, or holidays to limit the number of employees potentially exposed.  Work area must be curtained off to prevent contamination of adjacent areas.  The contractor shall utilize HEPA vacuums for the cleanup process.  See demolition requirements in sections S3.0  JOB HAZARD ANALYSIS (JHA) / ACTIVITY HAZARD ANALYSIS (AHA) and S11.0  PROTECTION OF PERSONNEL.

AQL:  No more than one valid complaint regarding contamination outside the work area.

(b) STD:  For floor modifications, the Contractor shall saw-cut the concrete floor inside the building at the required locations for the booth.  The contractor shall use a HEPA Vacuum with a Dust/Silica capture device when drilling or cutting concrete, in conjunction with applicable wet methods with appropriate additional housekeeping measures to ensure that any slurry generated by the wet control method is cleaned up when the work is completed to avoid a secondary dust exposure hazard.  The Contractor shall excavate the hole(s) to the required depth(s).  The Contractor shall supply and install the manufacturer specified steel reinforcements.  The Contractor shall supply, pour and level the concrete using manufacturer’s specified concrete ratings.

AQL:  Pass or Fail.

(c) STD:  For through-wall and roof penetrations, the Contractor shall patch with approved fire sealing material and insulation.  Additionally, roof penetrations shall be sealed and weather boots utilized to prevent leaks.  All ceiling and wall obstruction removals shall be the responsibility of the Contractor.  Prior to removal of wall and ceiling obstructions the Contractor shall notify and obtain approval from the COR.

AQL:  Pass or Fail.

5.2.3.2  Project Completion:  The Contractor shall complete all contractual work within the specified timeframe.

(a) STD:  All work must be completed within 360 calendar days from Notice to Proceed (NTP).

AQL:  Pass or Fail.

5.2.4  Training

5.2.4.1  Personnel Training:  The Contractor shall provide on-site training for Government personnel.

(a) STD:  Provide basic operation and PM training for up to six operators.

AQL:  100% of specified personnel trained.

(b) STD:  Provide maintenance and Lock Out / Tag Out training for up to four maintenance personnel.

AQL:  100% of specified personnel trained.

5.2.5  Documentation

5.2.5.1  Documentation:  The Contractor shall provide all required documentation prior to final acceptance of the project.

(a) STD:  Provide three hardcopies of O&M Manuals and Parts Manuals.  Provide three hardcopies of as-built CADD drawings in PDF, .dwg, and hardcopy formats.

AQL:  100% Compliance.

(Deliverable A.018)

5.2.6  Warranty

5.2.6.1  System Warranty:  The contractor shall provide a one-year warranty.

(a) STD:  Warranty covers all parts, labor, and travel for one year following final acceptance. Response time for warranty repairs is within 72 hours of notification.  Includes one annual PM service.

AQL:  100% Compliance.

5.3  Service Contract Reporting

5.3.1  System for Award Management (SAM) Service Contract Report (SCR):  The Contractor shall report ALL Contractor labor hours (including subcontractor labor hours) required for performance of services provided under this contract for the Sanding Booth via a secure data collection site.  The Contractor is required to completely fill in all required data fields through the following web address: www.sam.gov.  Reporting inputs will be for the labor executed during the period of performance during each Government fiscal year (FY), which runs from October 1 through September 30.  While inputs may be reported any time during the FY, all data shall be reported no later than October 31 of each calendar year.  Contractors may direct questions to the help desk by clicking “View Assistance for SAM.gov” which is located at the top of the SAM.gov website.  From there, you can the select “Contact Our Service Desk” which will allow you to contact SAM.gov directly.  If contract period of performance ends prior to September 30, the Contractor has 30 calendar days from end date of the contract to complete the SAM SCR requirement.

Steps for Submitting a Service Contract Report (SCR)

- Go to www.sam.gov and log in.

- Select Entity Registrations and then select Service Contract Reporting.

- SAM displays your entities which have service contracts and meet the reporting criteria. Select View by entity to see the service contracts for each entity.

- Next, select Add for the service contract against which you want to create a Service Contract Report.  Each service contract which meets the FAR Subpart 4.1703 reporting thresholds is displayed.

- You will be taken to the Complete Service Contract Report page. SAM displays the contract details and allows you to report. You are required to enter the following information:

- Total Amount Invoiced:  Total dollar amount invoiced for services performed during the previous Government FY under the contract (this amount should include the prime and any subcontract amount).

- Prime Contractor Hours Expended:  Prime contractor direct labor hours expended on the services performed during the previous Government FY.  The amount you enter is automatically divided by 2,080 hours to calculate a Full Time Employee (FTE) equivalent, displayed under the Prime Contractor Hours Expended as Prime Contractor FTEs.

- Report any required Tier 1 subcontractor information by selecting the Add Tier 1 Subcontract Information button.

- When you are ready to submit the report, select Submit.  This saves your report and returns you to the Select Service Contract page where you can create other SCRs or edit an existing SCR.

Steps for Editing a Submitted Report

- Follow steps 1-4 above.  Any previously submitted SCR will have a View/Edit button instead of an Add button.

- Select View/Edit.  You will be able to view the current SCR, edit available fields, and resubmit the record.  You can also delete previously entered information altogether.

STD:  All reporting information provided by the Contractor shall be accurate, complete, and not exceed suspense dates noted in corresponding paragraph above.

AQL: 100% Compliant

(Deliverable A.019)

PART 6

APPLICABLE PUBLICATIONS

6.  Applicable Publications (Current Editions):  The following publications, manuals, regulations, etc. are mentioned in this PWS and are listed below.

- Federal Acquisition Regulation concerning quality assurance (Revolutionary FAR Overhaul (RFO) FAR 12.208)

- Army Regulation for Antiterrorism (AT) Level I Training (AR 525-13)

- Army Directive and Regulation regarding security policies and access procedures (Army Directive 2014-05 / AR 190-13)

- Army Regulation for Operations Security (OPSEC) (AR 530-1)

- Department of Defense Manual for OPSEC training (DoDM 5205.02)

- DoD Instruction on Controlled Unclassified Information (CUI) (DoD Instruction 5200.48)

- Executive Order on Controlled Unclassified Information (Executive Order 13556)

- Code of Federal Regulations, Part 2002, regarding CUI (32 CFR Part 2002)

- Federal Acquisition Regulation for post-award conferences (FAR Subpart 42.5)

- Army in Europe Regulation for contractor identification (AE Reg. 27-715)

- Federal law regarding the protection of personal information (Privacy Act of 1974, Public Law 93-579, 5 U.S.C. § 552a)

- Federal Acquisition Regulation concerning Organizational Conflict of Interest (OCI) (FAR Subpart 9.5)

- Federal Acquisition Regulation clause for Accident Prevention Revolutionary FAR Overhaul (RFO) (FAR 52.236-13)

- U.S. Army Corps of Engineers Safety and Health Requirements Manual (EM 385-1-1)

- Occupational Safety and Health Administration standards for General Industry and Construction (OSHA 29 CFR 1910 & 1926)

- Installation-specific safety regulation (Tobyhanna Army Depot Safety Regulation 385-1)

- International standard for occupational health and safety management systems (ISO 45001)

- A set of codes and standards for fire safety (National Fire Protection Association (NFPA) Codes)

- A code for the design, construction, and maintenance of military facilities (Uniform Facilities Code (UFC))

- Specifications used for military construction projects (Unified Facilities Guide Specifications (UFGS))

- OSHA standards for fall protection in construction (OSHA 29 CFR 1926.500-503)

- OSHA standards for fall protection in general industry (OSHA 29 CFR 1910.28)

- Standard for Electrical Safety in the Workplace (NFPA 70E)

- Code of Federal Regulations concerning Army radiation permits (32 CFR 655)

- OSHA standard for the control of hazardous energy (Lockout/Tagout) (29 CFR § 1910.147)

- OSHA standard for respirable crystalline silica (OSHA 29 CFR 1926.1153)

- Code of Federal Regulations regarding the National Environmental Policy Act (32 CFR 651)

- Specification for asbestos abatement (United Facilities Guide Specification 02 83 14 00 10)

- Federal law regarding procurement of items with recycled content (Resource Conservation and Recovery Act (RCRA) Section 6002)

- Federal Acquisition Regulation provision for Recovered Material Certification (Revolutionary FAR Overhaul (RFO) Provision 52.223-4)

- Federal Acquisition Regulation clause for estimating recovered material content Revolutionary FAR Overhaul (RFO), FAR 52.223-9

- Federal law for the preservation of historical and archaeological sites (National Historic Preservation Act)

- Asbestos Abatement and Demolition/Renovation Notification Form (Pennsylvania Form 2700-FM-BAQ0021)

- Specification for building demolition (Unified Facilities Guide Specification 02 82 13.00 10)

- Standard for disinfecting water mains (American Water Works Association (AWWA) circular C651-14)

- Federal law for the conservation of threatened and endangered plants and animals (Endangered Species Act of 1973)

- OSHA standard for hazardous waste operations and emergency response (29 CFR 1910.120)

- Federal law addressing energy production in the United States (Energy Policy Act of 2005)

- Federal law to increase energy efficiency and the availability of renewable energy (Energy Independence and Security Act of 2007)

- Energy standard for buildings (ASHRAE 90.1)

- Code of Federal Regulations for the management of universal waste (40 CFR 273)

- Tobyhanna Army Depot regulation for its Environmental Management System (TYAD Regulation 200-5)

- Federal law protecting migratory birds (Migratory Bird Treaty Act of 1918)

- Federal law concerning energy efficiency (Energy Policy Act of 1992)

- EPA program for technician certification for handling refrigerants (EPA Section 608 Program)

- Regulations regarding hydrofluorocarbon refrigerants (AIM Act, Title 40, Chapter I, Subchapter C, Part 84)

- Pennsylvania state law related to waste management (PA Act 90)

- Code of Federal Regulations related to the Cybersecurity Maturity Model Certification (CMMC) (32 CFR part 170 and its sub-parts)

- Guide to Information Security Testing and Assessment (NIST Special Publication 800-115)

- Defense Federal Acquisition Regulation Supplement definition for Contracting Officer's Representative (COR) Revolutionary DFAR Overhaul (RFO), (DFARS 202.101)

- DoD Instruction for COR certification (DoD Instruction (DoDI) 5000.72)

- Federal Acquisition Regulation concerning the responsibilities of contracting officers Revolutionary FAR Overhaul (RFO), (FAR Subpart 1.602-2)

- Army Regulation for Management and Oversight of Service Contracts (Army Regulation 70-13)

- Federal Acquisition Regulation clause for Government Property Revolutionary FAR Overhaul (RFO), (FAR 52.245-1)

- Standard for electrical installation (NFPA 70, National Electric Code (NEC))

- Standards for ventilation systems (American Conference of Governmental Industrial Hygienists (ACGIH) Ventilation Design Criteria)

- UL Standard for Safety for Industrial Control Panels (UL-508A)

- Unified Facilities Criteria for Fire Protection Engineering for Facilities (UFC 3-600-01)

- OSHA exposure limits for shipyards (29 CFR 1915.1000 Table Z-Shipyards)

- OSHA exposure limits for mineral dusts (29 CFR 1910.1000 Table Z-3, Mineral Dusts)

- OSHA exposure limits for construction (29 CFR 1926.55 Table 1)

- Method for measuring airborne fiber concentrations (NIOSH Method 7400)

- Federal Acquisition Regulation for Service Contract Reporting Revolutionary FAR Overhaul (RFO), (FAR Subpart 4.1703)

PART 7

ATTACHMENT AND TECHNICAL EXHIBIT LISTING

7.  Attachment and Technical Exhibit List

7.1  Technical Exhibit A – Performance Requirements Summary

7.2  Technical Exhibit B – Deliverables Schedule

7.3  Attachment 1 – Estimated Workload Data

7.4  Attachment 2 – Historical Workload Data

7.5  Attachment 3 – Proposed Booth Configuration Diagram

7.6  Attachment 4 – Dust Explosivity Test Report

TECHNICAL EXHIBIT A

Performance Requirements Summary (PRS)

It bears noting that even if not all tasks from Part 5 Specific Tasks are captured in the PRS, it does not relieve the Contractor from complying with those tasks, and it does not preclude the Government from performing surveillance of those tasks.

| PERFORMANCE OBJECTIVE | STANDARD | PERFORMANCE THRESHOLD ACCEPTABLE QUALITY LEVELS (AQLs) | METHOD OF SURVEILLANCE |
| --- | --- | --- | --- |
| PRS#1 - Project Management and Design (PWS 5.2.1) | The contractor shall present an action plan within 15 calendar days of award. The contractor shall submit approved layout drawings within 45 days of award. | Zero Deviation from standard. | 100% Inspection |
| PRS#2 - Sanding Booth Design and Installation (PWS 5.2.2) | The contractor shall install new sanding booth to meet all specifications (dimensions, filtration, electrical, fire protection, etc.). | No deviation from contract specifications. | Periodic Inspection & 100% Final Inspection |
| PRS#3 - Site Work and Completion (PWS 5.2.3) | The contractor shall complete all contractual work within 360 calendar days of NTP. | Pass or Fail. | 100% Inspection |
| PRS#4 - Training (PWS 5.2.4) | The contractor shall train up to 6 operators and 4 maintenance personnel. | 100% of specified personnel trained. | Customer Feedback |
| PRS#5 - Documentation (PWS 5.2.5) | The contractor shall submit all required manuals and drawings prior to final acceptance. | Zero Deviation from standard. | 100% Inspection |
| PRS#6 - Warranty (PWS 5.2.6) | The contractor shall provide a one-year warranty. | Zero Deviation from standard. | 100% Inspection |
| PRS #5 - Service Contract Reporting (SCR) (PWS 5.3) | The Contractor shall completely fill in all the information in the format using the following web address www.sam.gov The contractor shall provide the estimated total cost (if any) incurred to comply with this reporting requirement. Reporting period shall be the period of performance not to exceed 12 months ending September 30 of each government fiscal year and must be reported by 31 October of each calendar year. If contract period of performance ends prior to September 30, the contractor has 30 days from end date of the contract to complete the SCR requirement. | Zero Deviation from Standard | 100% Inspection |

TECHNICAL EXHIBIT B

DELIVERABLES SCHEDULE

| Deliverable | Frequency | # of Copies | Medium/Format | Submit To |
| --- | --- | --- | --- | --- |
| A.001 - OPSEC Plan/SOP (1.6) | Once, required before handling any CUI; must be approved by the Government OPSEC Officer. | One each | Formal, documented plan. | To Government OPSEC Officer through COR |
| A.002 - CUI Disposition (1.6) | Once, upon contract completion. | All CUI returned to TYAD or destroyed | Return or destroy CUI per DoD/Army guidelines. | COR |
| A.003 - Key Personnel Names and CVs (1.10) | No later than the post-award meeting. | One each | In writing. | Contracting Officer |
| A.004 - Contractor Workspace Sign (1.12.1) | Within 10 calendar days after contract award. | One each | Proposed sign for review. | To the Contracting Officer through the COR |
| A.005 - ID Card Listing (1.12.2) | Prior to the contract performance date and updated as needed. | One each occurrence | A listing of issued ID cards. | Contracting Officer |
| A.006 - Non-Disclosure Agreements (1.18) | No later than 10 days prior to the commencement of work. | One each | Signed agreements. | Contracting Officer |
| A.007 - OCI Mitigation Plan (1.19) | Immediately upon becoming aware of a potential Organizational Conflict of Interest. | One each | Written plan. | Contracting Officer |
| A.008 - Accident Prevention Plan (1.21.1) | Before initiation of work at the job site. | One each | Written plan. | To Government Safety Office through COR |
| A.009 - Proof of Safety Notifications (1.21.1.2) | No later than 10 days after notifications are made. | One each occurrence | Documented proof. | To the Contracting Officer through the COR |
| A.010 - OSHA 30-Hour Course Certificates as part of Site Safety Plan (S1.0) | Before construction activities start. | One each | Certificates (as part of the site safety plan). | To Government Safety Office through COR |
| A.011 - Site-Specific Safety / Accident Prevention Plan (S4.0) | Prior to beginning activities. | One each | Written plan. | To Government Safety Office through COR |
| A.012 - Trenching Plans and Permits (S7.0) | Prior to any trenching works being performed. | One each occurrence | Plans, requests, and permits. | To Government Safety Office through COR |
| A.013 - Asbestos Abatement Work Plan (1.22.1) | Prior to beginning any asbestos abatement work. | One each | Written work plan. | To Environmental Branch (EB) through COR |
| A.014 - CMMC UID(s) (1.29(e)(1)(i)) | Prior to contract award. | One each | CMMC UID(s) from SPRS. | Contracting Officer |
| A.015 - Changes in CMMC UID(s) (1.29(e)(1)(ii)) | Throughout the life of the contract, as applicable. | One each | Updated CMMC UIDs. | Contracting Officer |
| A.016 - Action Plan and Timeline (5.2.1.1) | Within 15 calendar days of contract award (at post-award conference). | Two each | Written plan. | Contracting Officer and COR |
| A.017 - System Layout Drawing Package (5.2.1.2) | Within 45 calendar days of contract award. | One each | In .dwg and hardcopy format. | COR for approval |
| A.018 - O&M Manuals, Parts Manuals, & As-Built Drawings (5.2.4.2) | Prior to final acceptance of the project. | Three each | Hardcopies of manuals; PDF, .dwg, and hardcopy of drawings. | COR |
| A.019 - SAM Service Contract Report (SCR) (5.3.1) | Annually, no later than October 31; or within 30 days after end of contract. | N/A | Online submission at http://www.sam.gov. | http://www.sam.gov |

ATTACHMENT 1

ESTIMATED WORKLOAD DATA

| ## ITEM | NAME | ESTIMATED QUANTITY |  |
| --- | --- | --- | --- |
| 1 | Average Annual Number of Production Orders for fiberglass booth | eaches | 271 |
| 2 | Average Annual Labor Hours for fiberglass booth | hours | 3,959 |

ATTACHMENT 2

HISTORICAL WORKLOAD DATA

| ## ITEM | ## NAME | ## ESTIMATED QUANTITY |  |
| --- | --- | --- | --- |
| 1 | Total Number of Production Orders for fiberglass booth over a 5 year period | eaches | 1,355 |
| 2 | Total Number of Labor Hours for fiberglass booth over a 5 year period | hours | 19,798 |

ATTACHMENT 3

PROPOSED BOOTH CONFIGURATION DIAGRAM

ATTACHMENT 4

DUST EXPLOSIVITY TEST REPORT