## Sheet1
REQUIREMENTS LIST
Part Number | Description | Quantity | Unit of Issue
DS042AZA1E0 | Liebert CoolPhase Precision Cooling System (Specifications follow) | 4 | Each
Nominal 42 kW, 12 ton, floor mounted, downflow
Input Supply Voltage: 460 Volt, 3 Phase, 60 Hertz
65,000 amp RMS Short Circuit Current Rating
14 Gauge Welded Steel Frame with Autophoretic Coating
Frame can be field separated into three sections for transport through small areas.
Front Service Access Only
Supply Air Exits the Bottom of the Unit, Return Air enters through the Top of the Unit
| Backwards Inclined Fan with Variable Speed Direct Drive EC Motors, 4.2 HP | 1
Dual Refrigeration Circuits with Liquid Line Filter Driers, Refrigerant Sight Glasses, Expansion Valves and Liquid Line Solenoid Valves
| Independent Digital Scroll Compressors with Unloading Solenoid Valve | 2
Dual Refrigeration Circuits with Liquid Line Filter Driers, Refrigerant Sight Glasses, Expansion Valves and Liquid Line Solenoid Valves
A-Frame Evaporator Coil with Stainless Steel Condensate Pan
R-454B Refrigerant System, Field Supplied and Field Charged
Three-Stage, Finned Tubular, Stainless Steel Electric Reheat, Capacity: 25 kW
4" MERV 8 Filter Package
Liebert iCOM Microprocessor Control with High-Definition Display
Liebert iCOM Based BMS Communication
Base Comms & Connectivity includes one Ethernet port and one RS-485 port on iCOM controller, dedicated to supporting BACnet IP, Modbus TCP/IP, BACnet 485, Modbus 485 and SNMP v1/v2c/v3
Locking Disconnect Switch, Factory Installed
Exterior Panels Insulated and Powder Coated, Color: IBM Charcoal Gray
| 24” Adjustable Height Floorstand, per Unit | 1
| Liebert Point Leak Detection Sensor Kit, Model: LT410 | 1
MCS056E5AD | Vertiv CoolPhase Outdoor Air-Cooled Microchannel Condenser (Specifications follow) | 4 | Each
Input Supply Voltage: 460 Volt, 3 Phase, 60 Hertz
65,000 amps RMS Short Circuit Current Rating
Microchannel Aluminum Coil
Variable Speed EC Fans
Premium Electronic Control Board Providing Communication with iCOM using CANbus
Aluminum Exterior Panels
18” Aluminum Legs
**Must be an authorized reseller to quote**