| SUBJECT* | Lyons VAMC Water Heater Replacement Brand Specific to ensure hookups are compatible no additional piping being considered |
| --- | --- |

GENERAL INFORMATION

| CONTRACTING OFFICE’S ZIP CODE* | 12208-3410 |
| --- | --- |
| SOLICITATION NUMBER* | 36C24226Q0588 |
| RESPONSE DATE/TIME/ZONE | 05-11-2026 4pm EASTERN TIME, NEW YORK, USA |
| ARCHIVE | 99 DAYS AFTER THE RESPONSE DATE |
| RECOVERY ACT FUNDS | N |
| SET-ASIDE |  |
| PRODUCT SERVICE CODE* | 4520 |
| NAICS CODE* | 333414 |
| CONTRACTING OFFICE ADDRESS | Department of Veterans Affairs Samuel S. Stratton VA Medical Center 113 Holland Avenue (2-90NCA) Albany NY 12208-3410 |
| POINT OF CONTACT* | Contracting Officer Corey Swinton Corey.Swinton@va.gov |

PLACE OF PERFORMANCE

| ADDRESS | Lyons VAMC |
| --- | --- |
|  | 151 Knollcroft Road |
|  | Lyons NJ |
| POSTAL CODE | 07939-5001 |
| COUNTRY | USA |

ADDITIONAL INFORMATION

| AGENCY’S URL |  |
| --- | --- |
| URL DESCRIPTION |  |
| AGENCY CONTACT’S EMAIL ADDRESS |  |
| EMAIL DESCRIPTION |  |

DESCRIPTION

Qty – 1 Patterson-Kelley Model PK-08D Semi-Instantaneous Water Heater rated to

provide 27 GPM of Domestic Hot Water from 40-120F when supplied with 25 psig Inlet

Steam and 5 psig in the Coil @ 1122#/hr. Heater to be furnished with the following

features and controls to meet the specified demand:

- Solid Copper Nickel Pressure Vessel rated for 150 psi ASME working

pressure.

- Factory Insulation.

- 90/10 Double Wall Copper Nickel Tube Bundle rated for 150 psi ASME

working pressure and 210F test pressure.

- All bronze circulator pump, 1/6HP, NYC Trim Package, 115v/1ph/60Hz,

with isolation valves, ball and check valves, and venturi tees.

- 1 ½” Spence Pilot Operated, Self-Contained Steam Control Valve.

- 1 ½” Wye Strainer.

- ¾” ASME Temperature & Pressure Relief Valve at 150 psi.

- ¾” ASME Pressure Only Relief Valve (Shipped Loose).

- 1 ½” Float & Thermostatic Condensate Steam Trap & Strainer (Shipped

Loose).

- ½” Auxiliary Drip Tap (Shipped Loose).

- ¾” Drain Valve Factory Installed.

- Double Solenoid High Temperature Limit System with pre-wired control

box.

- Vertical Stand suitable for removal of heating section without

disconnection of domestic water lines.

- ¾” Vacuum Breaker Factory Installed.

- 3 ½” Dial Thermometer & Bundle Steam Pressure Gauge.

- Operation & Maintenance Manuals in electronic form.

- Factory Authorized Start-Up & Training

Tags: 276458 (WH-2)

Qty – 1 Patterson-Kelley Model PK-10D Semi-Instantaneous Water Heater rated to

provide 65 GPM of Domestic Hot Water from 40-140F when supplied with 40 psig Inlet

Steam and 25 psig in the Coil @ 3469#/hr. Heater to be furnished with the following

features and controls to meet the specified demand:

- Solid Copper Nickel Pressure Vessel rated for 150 psi ASME working

pressure.

- Factory Insulation.

- 90/10 Double Wall Copper Nickel Tube Bundle rated for 150 psi ASME

working pressure and 210F test pressure.

- All bronze circulator pump, 1/6HP, NYC Trim Package, 115v/1ph/60Hz,

with isolation valves, ball and check valves, and venturi tees.

- 2 ½” Spence Pilot Operated, Self-Contained Steam Control Valve.

- 2 ½” Wye Strainer.

- 1” ASME Temperature & Pressure Relief Valve at 150 psi.

- 1 ½” ASME Pressure Only Relief Valve (Shipped Loose).

- 1 ½” Float & Thermostatic Condensate Steam Trap & Strainer (Shipped

Loose).

- ½” Auxiliary Drip Tap (Shipped Loose).

- ¾” Drain Valve Factory Installed.

- Double Solenoid High Temperature Limit System with pre-wired control

box.

- Vertical Stand suitable for removal of heating section without

disconnection of domestic water lines.

- ¾” Vacuum Breaker Factory Installed.

- 3 ½” Dial Thermometer & Bundle Steam Pressure Gauge

.