# DRAFT

# Statement of Work (SOW)

# FACILITIES MAINTENANCE SERVICES

United States Coast Guard Training Center (TRACEN) Birmingham, AL

Table of Contents

1.	STATEMENT OF WORK	4

INTRODUCTION.	4

1.2.	GENERAL.	4

1.3.	OBJECTIVES.	4

1.4.	SITE DESCRIPTION.	4

2.	SCOPE	4

2.1.	TASK LIST.	5

2.2.	NORMAL WORKING HOURS.	5

2.3.	AFTER NORMAL HOURS CALLS.	5

2.4.	OVERTIME.	5

2.5.	FEDERAL HOLIDAYS.	5

2.6.	WORK COORDINATION.	6

2.7.	PERMITS.	6

2.8.	ACCESS TO BUILDINGS.	6

2.9.	CONTRACTOR OCCUPIED FACILITIES.	6

2.10.	CONTRACTOR SAFETY PROGRAM.	7

2.11.	HAZARDOUS MATERIAL / WASTE COORDINATOR.	8

2.12.	SAFETY DATA SHEET (SDS).	8

2.13.	TRAINING.	8

2.14.	ELECTRONIC DATABASE.	9

2.15.	CONTRACTOR PROPOSED CYBER / IT-RELATED SOLUTIONS.	9

2.16.	PESTICIDES/HERBICIDES LOG.	10

2.17.	PCBs.	10

2.18.	FIRE PREVENTION.	10

2.19.	CONSERVATION OF UTILITIES.	11

2.20.	ENVIRONMENTAL PROTECTION.	11

2.21.	PHASE-IN/PHASE-OUT PERIODS.	12

2.22.	KICK-OFF CONFERENCE.	13

2.23.	CONTINGENCES.	13

2.24.	WARRANTIES.	13

2.25.	CONTRACTUAL PROVISIONS.	14

2.26.	COORDINATION WITH GOVERNMENT PROJECTS.	14

2.27.	SUBCONTRACTOR(S).	15

2.28.	DAILY SYSTEMS REPORT.	15

3.	APPLICABLE DOCUMENTS.	15

4.	WORK PROCEDURES AND PRIORITIES	16

4.1.	GENERAL.	16

4.2.	CATEGORIES OF WORK.	16

4.3.	CONTRACTOR WORK CONTROL.	20

4.4.	WORK RECORDING AND FILING.	23

4.5.	PERFORMANCE OF WORK.	24

5.	SPECIFIC TASKS.	28

5.1.	SEWER SYSTEMS (SANITARY & STORMWATER).	28

5.2.	ELECTRICAL SYSTEMS.	29

5.3.	HVACR SYSTEMS.	31

5.4.	WATER DISTRIBUTION AND FIRE SUPPRESSION SYSTEMS.	33

5.5.	BUILDINGS AND STRUCTURES.	35

5.6.	CUSTODIAL.	40

5.7.	GROUNDS MAINTENANCE.	43

5.8.	REFUSE COLLECTION AND DISPOSAL.	49

5.9.	CAMPUS SECURITY	51

5.10.	PEST CONTROL.	52

6.	DELIVERABLES.	57

7.	PERSONNEL REQUIREMENTS/QUALIFICATIONS	59

7.1.	ADMINISTRATION AND MANAGEMENT.	59

7.2.	PERSONNEL.	59

7.3.	OTHER PERSONNEL.	61

7.4.	CONTRACT EMPLOYEES.	61

7.5.	ABILITY TO COMMUNICATE.	62

8.	GOVERNMENT QUALITY ASSURANCE	63

8.1.	REWORK/REPERFORMANCE.	63

8.2.	EQUIPMENT.	63

8.3.	SUPPLIERS’ CATALOGS.	65

8.4.	UTILITIES.	65

8.5.	COMMUNICATION FREQUENCIES.	65

8.6.	MAINTENANCE CART OPERATION.	65

# STATEMENT OF WORK

INTRODUCTION.   The purpose of this contract is to provide facilities maintenance, landscaping, janitorial, refuse collection, and security services at the former Birmingham-Southern College campus in Birmingham, AL. The 192-acre campus is comprised of a variety of structures to include, but not limited to, family housing, barracks, office buildings, warehouses, academic buildings, pools, fitness facilities, recreation facilities and appurtenances serving the Coast Guard and other Government agencies.

  - GENERAL.  The Contractor shall operate, maintain, repair, improve, alter, and construct real property facilities, improvements, and equipment, and provide related services as specified, in strict accordance with all terms and conditions contained herein. The contractor must operate and perform all work in accordance with applicable national codes; industry standards and best management practices; relevant technical manuals and publications; manufacturer’s recommendations; Federal, State, and local laws and regulations; and pertinent Department of Homeland Security, U.S. Coast Guard, and Shore Infrastructure Logistics Center instructions, regulations, policies, and practices. All work must be performed at the former Birmingham-Southern College campus in Birmingham, Alabama.  The period of performance for this work is 1 year from date of award.  A one-year option period may be exercised.

OBJECTIVES.  The objective of this contract is to ensure continued campus maintenance, security, janitorial, landscaping, and refuse collection services in support of Coast Guard missions. This contract requires preventative maintenance, repairs, and minor improvements to be performed at or above the commercial standard. All tasks under this contract must be performed in accordance with all applicable codes, laws, regulations, and policies at all levels. The contractor must place the highest emphasis on ensuring academic and lodging facilities are safe for operation to include heating, cooling and electrical environment for these facilities are within parameters established by this contract, DHS, USCG and commercial best practices.

  - SITE DESCRIPTION.  The former Birmingham-Southern College campus occupies a site of approximately 192 acres of land on Arkadelphia Road; seven miles west of Birmingham-Shuttlesworth International Airport in Birmingham, AL. The Training Center site is a college campus, bounded on the north by Interstate Highway 20, Arkadelphia Road on the east, and 8th Avenue West on the south.

TRAINING CENTER MISSION.  This site will be the newest established Coast Guard training center.  Training center missions are to train Coast Guard Active Duty, Reservists, Auxiliarists and civilians in the latest techniques and applications of the modern Coast Guard. Training Centers frequently also offers basic and advanced courses to personnel from other armed services, State and Federal agencies, and allied nations throughout the world.

# SCOPE

The Contractor shall provide all personnel, planning, programming, administration and management services and supplies required for the maintenance and repair of all designated buildings, structures, utility and sewage systems, other real property, janitorial, grounds maintenance and pest control services to include the moving and handling of government- owned furnishings, to ensure the adequate and timely completion of all work is accomplished. This document provides the minimum requirement for this contract.

  - TASK LIST. The following task list was generated for this effort to provide facilities maintenance. Tasks will include the following:

- Heating, Ventilation, and Air Conditioning Systems

- Electrical Systems

- Fire Alarm/Suppression Systems Equipment

- Custodial Services

- Building Structures

- Water Distribution Systems

- Sewer Systems

- Pest Control

NORMAL WORKING HOURS.  Unless otherwise specified or with verbal authorization from the Facilities Engineer, the Contractor must perform all routine inspections, preventive maintenance, repair work, and custodial work during normal working hours, 7:00 a.m. to 5:00 p.m., Monday through Friday, except Federal holidays. Workdays shall be comprised of 8 consecutive hours to start no later than 9:00 a.m. and to conclude no earlier than 3:00 p.m.  Any work which will cause a disruption of utility service or otherwise make the facility unusable by its occupants may, with the Facility Engineer’s permission, be performed outside of normal working hours at no additional cost to the Government.  Additional emergent work may be required outside normal working hours.  Work performed outside normal working hours may be tracked and reduced from the next available workday with Facility Engineer approval.

AFTER NORMAL HOURS CALLS.  The Contractor shall designate two key personnel with appropriate authority who can be reached immediately by telephone to respond to emergency situations 24 hours per day, 7 days per week in accordance with the response times identified in Section 5.2.2.3. See Section 5.3.8 in reference to point of contact for emergency work.

OVERTIME.  The contractor is required to provide 24-hours per day, 7-days-per-week performance; however, this contract does not compensate for overtime.  Work hours performance may be shifted with Facility Engineer’s approval in response to emergent or after-hour work performance.

FEDERAL HOLIDAYS. Normally, routine work must not be scheduled on Federal holidays. When holidays such as July 4th or Columbus Day occur on a weekend, the Federal holiday will occur on either the preceding Friday or the following Monday. If the contractor wishes to work on a federal holiday, written approval should be submitted 48 hours prior to the holiday. The Facilities Engineer may approve a contractor’s written request to work on a federal holiday if the situation warrants such work, it cannot be performed during regular hours, and it is performed at no additional cost to the government.

WORK COORDINATION.

OCCUPIED AREAS. Government personnel work in occupied areas during normal working hours. The Contractor’s work must not unduly interfere with Government work in the area. The Contractor shall report any interference problems between the Government and the Contractor to the Facilities Engineer for resolution. The Contractor shall not interrupt classes in session to perform work unless approved in advance by the Facilities Engineer. The Contractor may have to schedule access to classrooms prior to performing work. Some work in classrooms may have to be performed after normal working hours due to unavailability of the space for Contractor’s use. The Contractor shall not commence work that will prevent the normal use of any occupied area (e.g., administrative offices) without having previously received approval from the Facilities Engineer at least 48 hours in advance. This requirement does not apply to emergency work.

FACILITY CLOSURES.  The Contractor shall submit a Facility Closure Request to the Facilities Engineer for approval 14 calendar days prior to closing any facility or part of a facility for work required to be performed. Responsibility for coordinating access to closed facilities resides with the Contractor.

SECURING UTILITIES. The Contractor shall submit a Utility Outage Request to the Facilities Engineer for approval 14 days prior to securing any utility (water, heat, air conditioning or electricity) to any structure, space or facility. This restriction is waived for emergency situations where the delay associated with notification of the Facilities Engineer will cause injury or significant damage to Government property. The Facilities Engineer must be immediately notified of any such action taken.

PERMITS.  The Contractor shall obtain, without additional cost to the Government, all appointments, licenses, and permits required for the performance of work and for complying with all applicable Federal, State, and Local laws. Copies of permits and licenses must be provided to the Facilities Engineer prior to contract start date or before work requiring a permit commences.

ACCESS TO BUILDINGS. The Contractor shall obtain access to buildings and arrange for the buildings (other than Government-provided facilities) to be opened and closed as necessary for the performance of work. Whenever a key is issued to contract workers, the key must be signed out and in by the requesting party. Contractor must ensure that sufficient arrangements are made for security of the building(s) at the end of each workday. No buildings should be open, or spaces occupied after NORMAL WORKING HOURS without the knowledge of campus security.

CONTRACTOR OCCUPIED FACILITIES. The Contractor is responsible for the security of all Government provided facilities, materials, and equipment. The Contractor is responsible for and shall maintain all shops and areas used by the Contractor in performance of the contract, in a clean, neat, orderly, and sanitary condition. Work areas must be kept clutter free and swept daily. All housekeeping supplies and related consumable tools, such as drill bits, saw blades, etc., must be provided by the Contractor at their expense. The premises must be kept free from accumulation of waste material and trash resulting from work at all times. Combustible materials must be removed daily. Contractor occupied facilities located on Government property are subject to material, fire and safety inspection by the Facilities Engineer. Any fire or safety hazards noted in the inspections produced by Contractor action or inaction must be Corrected by the Contractor at no cost to the Government.

CONTRACTOR SAFETY PROGRAM. All work shall be conducted in a safe manner and must comply with all applicable federal, state and local safety standards and requirements. The Contractor shall employ a full time, on-site safety manager capable of enforcing all applicable safety practices. The safety manager is responsible for ensuring all work is performed and completed in compliance with the contractor’s safety plan, all applicable federal, state and local safety standards and requirements, and contract requirements. The Government reserves the right to inspect for compliance with safety standards and requirements. Prior to commencement of work, the Contractor shall meet with the Facilities Engineer and other Government Representatives to discuss and develop mutual understandings relative to the administration of the Safety Program. The Safety Program shall include the following as a minimum:

    - CONTRACTOR SAFETY PLAN. The Contractor shall develop and submit a Safety Plan within 14-calendar days of this Statement of Work being placed into effect and whenever changed by the Contractor. The Contractor’s safety plan shall comply with all Federal and State laws, including OSHA and regulations set forth in 29 CFR 1910, 29 CFR 1926, 29 CFR 1940 and 29 CFR 1946 and in Commandant Instructions M5100.47 and M11000.11.

    - ACCIDENT PREVENTION. The contractor shall comply with all federal, state and local regulations concerning accident prevention. The contractor shall maintain a record of property damage, accidents, and fires caused by the Contractor or subcontractor employees. The Contractor shall report damage, fires, or accidents to the Facilities Engineer IAW Homeland Security Acquisition Regulation Clause HSAR 3052.223-90. The Contractor shall comply with all mishap reporting procedures found in the latest edition of COMDTINST M5100.47. These procedures are for information and data gathering purposes only. The Government will supply the Contractor with the necessary forms and instructions for completion of the forms. All mishaps must be reported to the FACILITIES ENGINEER immediately and in writing within 24 hours.

    - PRESERVING AND REHABILITATING HISTORIC STRUCTURES. Work performed on this contract has the potential to affect a property listed in or eligible for the National Register of Historic Places.  To avoid these effects, and to ensure compliance with the National Historic Preservation Act, work shall be executed in strict accordance with The Secretary of the Interior's Standards for the Treatment of Historic Properties, with Guidelines for Preserving, Rehabilitating, Restoring & Reconstructing Historic Buildings (Treatment Standards) as published by the National Park Service. The contractor is to use the treatment standards that apply to each specific task. All actions shall be undertaken with the gentlest means possible to prevent damage to historic materials. If in the process of executing this contract damage is inadvertently caused, or damage is found, the Contractor shall stop work and immediately notify the Contracting Officer’s Representative.  The Contractor shall submit within the work plan all plans, materials, and methods necessary to fulfill the work underneath this contract in consideration of the Treatment Standards for approval by the Contracting Officer’s Representative.

    - HANDLING AND CONTROLLING HAZARDOUS OR TOXIC MATERIALS INCLUDING ASBESTOS. Under this contract there are two categories of hazardous or toxic material. The first category, Contractor-owned or generated hazardous or toxic material includes material either brought on site by the contractor or contractor’s subs to perform duties or those generated by the Contractor’s or Contractor’s sub actions. The contractor is solely responsible for Contractor-owned or generated hazardous material. This includes any hazardous material encountered while performing maintenance and repairs specified wherein. The Contractor’s Safety Plan shall contain a section specifically addressing the use, handling procedures and disposal of all hazardous materials that are likely and foreseeable to be encountered as part of this contract, including asbestos, lead and lead-based paint, and PCBs. The Contractor is solely responsible for this category of hazardous or toxic material. The second category, existing hazardous or toxic material, includes hazardous or toxic materials encountered while performing maintenance and repairs specified herein. For this second category the Contractor must notify the Facilities Engineer immediately and handle the materials for the government in accordance with the Facilities Engineer’s direction.

  - HAZARDOUS MATERIAL / WASTE COORDINATOR. The Contractor shall designate in writing a Hazardous Material/Waste Coordinator to manage all Hazardous Materials. This individual shall maintain the contractor’s Safety Data Sheets (SDS), as required by HSAR Clause 3052.223-70, Removal or Disposal of Hazardous Substances – Applicable Licenses and Permits, and provide any Hazardous Material information required/requested by the Facilities Engineer, and participate in HAZMAT program meetings (generally held quarterly on site). Handling and disposal of the materials shall comply with all federal, state, and local regulations.

SAFETY DATA SHEET (SDS). The Contractor shall request a SDS from their supplier for each chemical item used at TRACEN. Prior to ordering this material, the Facilities Engineer must review and approve all new chemical products. These sheets must then be placed in the Contractor’s hazardous material data sheet file.

TRAINING. The Contractor shall provide all necessary training, materials, and equipment required for their personnel to properly handle Hazardous Materials. The Contractor’s Hazardous Materials program shall be managed by IAW Emergency Right-to-Know-Act (EPCRA) requirements. The Contractor shall abide by all 40 CFR 350-372 (EPA) and 20 CFR 1901.1-1910 (OSHA) requirements.

ELECTRONIC DATABASE. The Contractor shall develop and maintain an electronic database or spreadsheet utilizing Microsoft Office software to monitor hazardous material inventories and purchases. Contractor shall electronically track and maintain the following information for each Hazardous Material Used: SDS ID #, Point of Contact, Product Name, Manufacturer, Manufacturer’s Address, Manufacturer’s Phone #, Vendor, Vendor’s Address, Vendor’s Phone #, NSN/Part #, Physical State, Qty on Hand, Max Quantity, Units of Measure, Container Type, Container Size, Location (BLDG), Room #. The contractor shall always make these reports available as requested by the Facilities Engineer. The contractor shall submit quarterly updates on the first workday of January, April, July and October.

CONTRACTOR PROPOSED CYBER / IT-RELATED SOLUTIONS.  The contractor shall identify all cyber/IT-related hardware, software and/or services that are included as part of its solution to the government’s requirement to store or process Coast Guard data or connect to Coast Guard networks or other assets. The offeror or contractor shall provide this information in an electronic delimited file format (for example, csv file, docx table, xlsx table, rtf table or HTML file) as follows in its government response to the solicitation.  No cyber or IT related materials shall be purchased on behalf of or installed on Coast Guard properties without written approval from the Facilities Engineer.

Contractor Proposed Cyber/IT Related Solutions for CG-6 Review

| Product | Manufacturer | Version | Release | Quantity | Brief | Cost | Recurring |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Name | or Company | (if any) | (if any) | (if any) | Description | (If not FFP. | or Non- |
| or |  |  |  |  |  | Contractor | Recurring? |
| Service |  |  |  |  |  | is | If |
|  |  |  |  |  |  | responsible | recurring, |
|  |  |  |  |  |  | for also | state |
|  |  |  |  |  |  | ensuring | frequency |
|  |  |  |  |  |  | inclusion in |  |
|  |  |  |  |  |  | the cost |  |
|  |  |  |  |  |  | proposal) |  |

PESTICIDES/HERBICIDES LOG. The Contractor shall maintain a certified applicator log of all pesticides and herbicides applied on the Training Center, the date and amount of application (with signature of certified applicator), and provide a copy of the log to the Facilities Engineer upon request. This log shall be turned over to the Government within 5 days of completion or termination of the contract.

PCBs. The Contractor shall comply with current regulations used by the Environmental Protection Agency and State of Alabama for handling Polychlorinated Biphenyl (PCB). The Toxic Substance Control Act establishes PCB controls by regulations contained in 40 CFR 761.1 (see Paragraph 6). The Contractor shall provide all materials and equipment for personnel handling PCB.  All existing PCBs on campus shall be properly disposed of.

FIRE PREVENTION. The Contractor shall establish and maintain a fire prevention program to comply with the provisions of current Government regulation, OSHA, National Fire Codes, sound industrial practices, as well as other fire prevention regulations, manuals and/or codes cited throughout this contract and applicable to specific industrial-type functions. The Fire Prevention Program must be included in the Contractor’s Safety Plan. The Government reserves the right to inspect facilities for fire prevention, evaluate through drills, and to enforce compliance. All individuals performing inspection, testing and maintenance of fire alarm and fire protection systems must meet the requirements stated in NFPA 72, Chapter 10.2.2.5.1 and be NICET Level II certified.

    - CONFINED SPACE ENTRY (CSE) PROGRAM. The contractor shall establish and maintain a Confined Space Entry (CSE) program IAW the 29 CFR 1910.146 and current government regulations (i.e., COMDTINST 5100.48(series). The contractor shall designate in writing to the Facilities Engineer competent person(s) as defined in 29 CFR 1910.146 and provide documentation of their qualifications to the government. The CSE program shall be included in the contractor’s Safety Plan. The contractor shall ensure its employees are properly trained concerning workplace-confined spaces. The contractor shall ensure that the employees are experienced with the conditions and confined workspaces prior to beginning work. The contractor shall coordinate entry operations with the Safety Officer. The government reserves the right to inspect spaces to ensure the proper procedures are being always followed.

    - SAFETY EQUIPMENT. The Contractor shall provide their employees with all personal protective equipment (PPE) required to safely accomplish all tasks. PPE includes but is not limited to protective clothing, hearing protection, respiratory protection, tripod and mechanical winch, atmospheric testing equipment, etc. The Contractor’s employees shall use required PPE, clothing and/or use equipment appropriate to the work being done at all times. The contractor is responsible for ensuring that all personnel required to wear or use any respiratory protection are properly trained in its use and limitations and are medically screened and fit tested. In the event of hazardous conditions in a permit-required space, the contractor shall contact the Safety Officer and Facilities Engineer to advise them of the situation.

    - RESULTS OF SAFETY NONCOMPLIANCE. If the Contractor fails or refuses to promptly comply with safety requirements, the Facilities Engineer may issue an order stopping all or part of the work until the Contractor takes satisfactory corrective action. No part of the time lost due to any such stop order shall be made the subject of claim for extension of time or for excess costs or damages to the Contractor.

  - CONSERVATION OF UTILITIES. The Contractor shall develop an energy conservation plan. The plan shall include, but is not limited to, the following items. Evaluate and recommend measures that can be taken to:

- Reduce general operating cost.

- Minimize energy usage.

- Add insulation or make other changes for savings.

- Use timing or cycle-control devices to promote energy savings.

- Recommending the use of energy efficient materials and equipment.

- Instructing Contractor personnel in utilities conservation practices and requiring them to operate under conditions which preclude waste of utilities.

    - HVAC CONTROLS. Controls for heating, ventilation, and air conditioning systems shall be adjusted only by workers with the skills and qualifications necessary for maintaining and repairing the systems. The Contractor shall set proper temperature settings as defined by the Facilities Engineer.

  - ENVIRONMENTAL PROTECTION. The Contractor shall comply with all applicable Federal, State, and Local laws, regulations, and standards regarding environmental protection. Inspection of Government facilities operated by the Contractor may be accomplished by authorized State and Federal officials on a no notice basis. The Contractor shall make all spaces available for inspection during normal working hours.

    - NON-COMPLIANCE CITATIONS. Citations of Contractor-operated Government-provided facilities for noncompliance with environmental standards are a matter for resolution between the Contractor and the issuing office of EPA or State of Alabama regulatory authorities. The Contractor shall be responsible for/pay any fines, penalties or charges associated with citations issued by Federal, State or Local officials for noncompliance with environmental standards. If the citations are issued against the Government due to the Contractor’s action or inaction, the Facilities Engineer will deduct the fine from any funds due to the Contractor. The Facilities Engineer may order work to be performed by the Contractor to correct a pre-existing non-compliant situation. The Contractor will not be held responsible for payment of citations issued because of conditions created by the government’s actions or inactions. The Contractor is responsible for achieving compliance with environmental standards within 18-months of this statement of work being placed into effect.  If compliance cannot be achieved due to major repairs or improvements that exceed this statement of work, the contractor shall advise the Facilities Engineer, Facilities Engineer’s Representative, and Facilities Engineer. This notification shall include required repairs or improvements and a level 1 cost estimate for those repairs.

    - INSPECTION BY REGULATORY AGENCIES. The Contractor shall notify the Facilities Engineer immediately of any inspection visit, planned or unplanned, by an agent or agents of any Government regulatory agency. The Facilities Engineer will issue instructions as to how to proceed in cooperating with the inspector. The Contractor shall submit a written report to the Facilities Engineer, by close of business of the next working day following completion of the inspection/visit. The report shall include the names, identification numbers, agency of the inspectors, and the reason for the visit. A copy of any reports received, and samples collected, if provided by the agency, shall be included with the contractor’s report. Samples shall be accompanied by a statement signed by the agency inspector validating their authenticity.

  - PHASE-IN/PHASE-OUT PERIODS.

The Contractor shall develop a phase out plan with their 3-month prior to the conclusion of the base period of performance. The phase-out plan shall describe actions, plans and procedures to ensure a smooth transition to future operators and maintainers, file transfer, and document preservation.  The plan shall be submitted to the Facilities Engineer for review and approval 90 days prior to conclusion of the base period of performance. The final phase-out portion of the plan must be updated 30 days prior to completion of the contract.

    - PHASE-IN. The service provider shall assume total responsibility for all operations required by this statement of work at time of implementation. A fully qualified and capable of performing all work required under this statement of work, as well as all equipment, tools, materials and supplies to ensure capability of performing contract requirements within 60 calendar days.

    - PHASE-OUT PERIOD. The Contractor shall present a detailed plan for any phase-out period, regardless of precipitating reasons. The plan shall include procedures for minimizing impact on performance in compliance with standards in the contract. The plan shall also (1) present procedures for retaining the required staffing level (including key personnel) necessary to provide complete contractual support through expiration of the contract and (2) describe in detail how responsibility and accountability will be relinquished for all Government-provided items. Beginning 30 calendar days immediately prior to the end of the contract period, the Contractor will be required to allow personnel from the Government and/or from a successor contractor to observe daily operations covered under this contract. During this “phase-out” period the Contractor will remain totally responsible for the services required in this contract. The Contractor shall not defer any needed repairs or maintenance for the purpose of avoiding responsibility to the successor contractor. The Contractor shall coordinate activities with the incoming Contractor to affect a smooth and orderly transition at the end of the period. The Contractor shall remove all Contractor-owned equipment, tools, parts and belongings from the Government-provided facilities by midnight on the last day of performance. The Contractor shall provide on-the- job familiarization for the incoming Contractor as required.

  - KICK-OFF CONFERENCE. The Contractor shall meet in conference with the Facilities Engineer and Program Manager as well as other authorized representative(s) of the Government at the former site of Birmingham-Southern College to discuss and develop mutual understandings relative to scheduling and administration of work performed under this contract.

  - CONTINGENCES. The Coast Guard shall plan how it will meet mission requirements in the event of a national emergency or natural disaster. The Coast Guard must be able to react to such events without undue delay. Sudden or unusual events may result in a substantial impact on the Contractor’s performance and contract requirements. If contingencies such as those specified below develop, the Contractor shall continue to perform contract work. Some examples of contingencies are as follows:

- A national emergency entailing sudden buildup of military forces that increases contract requirements.

- A natural disaster (e.g., snowstorm, hurricane, flooding) that impacts upon the Contractor’s ability to perform this contract and the Coast Guard’s ability to perform its mission.

- A labor strike that impacts upon Contractor’s ability to perform.

    - CONTINGENCY PLAN. The Contractor shall submit a comprehensive Contingency Plan with-in 30 days of start of performance.  The contractor’s plan shall outline at the minimum the methods the Contractor will use to meet contract requirements in emergency situations cited above.

  - WARRANTIES. The Contractor shall be responsible for exercising all manufacturers’ commercial warranties on Government equipment, parts, roofs and systems under this contract. The Contractor shall report to the Facilities Engineer any difficulty in exercising manufacturer warranties and request the Facilities Engineer’s assistance as necessary. Existing warranties, if any, will be provided to the Contractor by the Government prior to contract start date.

    - The Contractor shall maintain a file of the original warranties on new equipment installed. The contractor shall also establish and maintain a list of manufacturers’ telephone numbers and points of contact for all warranted equipment. A copy of this list must be provided to the Facilities Engineer whenever new equipment is added, or warranties expire. All warranties shall list the Government as the equipment owner.

    - Government equipment installed by the Contractor that fails within a warranty period due to Contractor’s poor workmanship, or by not following manufacturer’s installation, operation or maintenance instructions, shall be replaced or repaired at the Contractor’s expense. This determination will be made by the Facilities Engineer and Facilities Engineer.

    - Warranted equipment and component parts thereof shall not be repaired, removed or replaced by the Contractor while under warranty of the manufacturer or the installer; all defects in workmanship or materials, defective parts or improper installation found by the Contractor shall be reported in writing or electronic correspondence to the Facilities Engineer. The Contractor shall take actions necessary to exercise the warranty. The Contractor shall be responsible for knowledge of the equipment and components that are covered by original warranty and the duration of the warranty.

    - The Contractor shall perform all preventative maintenance on warranted equipment in accordance with the manufacturer’s warranty as well as that recommended by current year, RS MEANS, Facilities Maintenance & Repair Cost Data. The contractor shall also be responsible for coordinating repair or replacement of all non-warranted component parts on all warranted equipment.

  - CONTRACTUAL PROVISIONS. The Contractor shall promptly inform the Facilities Engineer in writing or electronic correspondence of any circumstances, directives, regulations or references which conflict with the requirements of this statement of work. When there is substantial doubt as to the exact meaning of any specification, the contractor shall request in writing or electronic correspondence an interpretation from the Facilities Engineer. When the Contractor finds that a specification standard, technical exhibit, directive or reference shall be modified for application to a particular working condition or circumstances, the Contractor shall request approval from the Facilities Engineer of the alternative approach which meets the intent and scope of this contract. Under no circumstances may safety standards be compromised.

  - COORDINATION WITH GOVERNMENT PROJECTS.  The

Contractor’s Project Manager and employee(s) knowledgeable with each specific system shall be available to discuss the operation, maintenance, and repair of facilities and systems with Government Engineers/Architects involved in design of new or rehabilitation projects. Meetings will be held at the former Birmingham-Southern College site and coordinated by the Facilities Engineer. The estimated frequency of such meetings is six per year. Meetings and discussions between the Contractor and Facilities Engineer concerning work requests are not considered projects under this Paragraph.

    - SYSTEMS OPERATION. The Contractor shall exercise/operate systems, when directed by the Facilities Engineer, for purpose of Government personnel familiarization and project/design development. The estimated frequency is six per year. This does not include operation required to ensure the Contractor’s compliance with the requirements of this work statement.

  - SUBCONTRACTOR(S). If subcontractor(s) are retained, five (5) days prior to subcontractor start date, the Contractor shall submit a list of all its subcontractors including the name, point of contact, address, and telephone number. This list shall be updated and submitted to the Facilities Engineer semiannually and within two (2) days of any additions or deletions to the subcontractor list. The subcontractor(s) shall comply with all contractual requirements of this work statement. The contractor is fully responsible for the actions/failure to act of their subcontractors.

  - DAILY SYSTEMS REPORT. The Contractor shall submit to the Facilities Engineer a list of all building systems or utilities that are not fully operational at 4:00 pm each workday. The list must include facility name, system affected and cause of failure and estimated date of repair.

# APPLICABLE DOCUMENTS.

The Contractor shall comply with all federal, state, local laws and regulations, industry standards/references, and the Coast Guard regulations and instructions. The list below is not all inclusive. The Government will furnish, or make available for contractor use, the documents described below. All referenced Federal laws, codes, directives, instructions, etc. in force at time of the contract must be considered mandatory as applicable to the service or function to be performed. The Contractor shall ensure that all publications received are kept current.

| Publication Number | Title | Date |
| --- | --- | --- |
| COMDTINST M5100.(series) | SAFETY (COAST GUARD) AND ENVIRONMENTAL HEALTH MANUAL | 2016 |
| COMDTINST M6000.(series) | MEDICAL MANUAL, CHAPTER 7 | 2014 |
| COMDTINST 10360.(series) | REGULATIONS GOVERNING VOC EMISSIONS AND SOLVENT CONTENT IN PAINTS, COATINGS, SOLVENTS, ADHESIVES AND CLEANERS’ MANUAL | 2014 |
| COMDTINST M11000.(series) | FACILITIES ENERGY MANUAL | 1999 |
| COMDTINST M11000.(series) | CIVIL ENGINEERING MANUAL | 2014 |
| COMDTINST M11240.(series) | MOTOR VEHICLE MANUAL | 2017 |
| SILC-JG-36-11 27 11 00-01 | FACILITY ENGINEERING MANAGEMENT GUIDE | 2018 |
| 3072.2(series) | KEY CONTROL | Current |
| 3470.1(series) | SNOW REMOVAL BILL | Current |
| 5060.1(series) | DISPLAY OF FLAGS & PENNANTS | Current |
| 5100.48(series) | CONFINED SPACE ENTRY | Current |
| 5355.3(series) | ADMINISTRATIVE ACTION & FOLLOW- UP PROCEDURES FOR SUBSTANCE ABUSE SITUATIONS & INCIDENTS | Current |
| 5510.3(series) | AUTHORIZATION FOR UNANNOUNCED VEHICLE INSPECTIONS | Current |
| 5560.1(series) | MOTOR VEHICLAE & PARKING REGULATION | Current |
| 6260.2(series) | PPE | Current |
| 6260.1(series) | ASBESTOS MANAGEMENT | Current |
| 11100.1(series) | FACILITIES INSPECTIONS | Current |
| 11320.1(series) | FIRE PREVENTION PROGRAM | Current |
| 16455.1(series) | OIL SPILL PREVENTION | Current |

# WORK PROCEDURES AND PRIORITIES

  - GENERAL.  The Contractor shall be responsible for performing work to support all facilities, including the collateral and non-collateral equipment. Work may be required on buildings (e.g. small storage buildings), equipment (i.e. water fountains, small refrigerators, etc.), or structures not specifically listed. The Contractor shall provide all management required to perform all work in accordance with industry standards and federal, state, local laws and Coast Guard regulations. Documents referenced in Section 4 above are not necessarily all-inclusive. Requirements stated as advisory or permissive in referenced publications are mandatory for purposes of this contract, except where there are documented current in-house practices to the contrary, where the requirements are commercially impractical, or where the Facilities Engineer determines that such requirements will serve no useful purpose.

    - PERSONAL SERVICES PROHIBITION. Any language about supervision in the referenced publications list in the section above shall not be taken as authorizing personal services.

  - CATEGORIES OF WORK. There are three categories of work, Level 1 – Preventative Maintenance, Level 2 – Work Orders, and Level 3 Job Orders as follows:

    - LEVEL 1 - PREVENTATIVE MAINTENANCE. The Contractor is responsible for performing all work IAW the contract statement of work, including preventive maintenance in accordance with industry standards, as a minimum standard (RS MEANS) and manufacturers’ recommendations, and Contractor prepared frequency schedule approved by the Facilities Engineer.  No task orders or approvals are required for Contractor performance of preventative maintenance once the Contracting Officer’s Representative approved the required work plans that identify all plans, materials, and methods necessary to fulfill the work underneath this contract in accordance with the Treatment Standards for Historic Properties.

    - LEVEL 2 - WORK ORDERS, MATERIAL COSTS GREATER THAN $2,500 AND UNDER $50,000. The Facilities Engineer or other designated Government representatives will issue work orders to repair, construct, install, remove, alter, improve, replace, add, or overhaul any facility, grounds, or equipment covered by this contract. This requirement may pertain to the procurement and installation of new equipment/building fixtures, structural components, or other associated materials that may be necessary for mission performance. Identical work items must be submitted in the same work order for work within a single building. Identical work has the same character and requires the same trade and material. For example, replacing carpet and painting are not identical, while exterior painting of the northern and southern exposures of a building are identical. Installation of a new electric outlet may involve multiple trades, but all work associated with the installation of the outlet must be on one work order. Discrepancy items noted during a government inspection of any building, grounds, or equipment must not be grouped unless they are identical. Work identified by the Contractor or Facilities Engineer that requires a combined acquisition of materials and/or subcontractor labor in excess of $2,400 must be reported to the Facilities Engineer upon discovery.  All work orders with a combined material and/or labor cost between $2,500 and $50,000 must receive written approval prior to start.

Performance of Level 2 Work Orders are factored into the staffing model detailed within this statement of work.  No additional costs for labor are anticipated in conjunction with Level 2 work orders.  If subcontractors are required for the performance of a work order, the Facilities Engineer must be notified, and written approval must be received prior to retaining subcontracted work.  Material and subcontractor costs incurred for all work orders are expected to remain under $1,500,000 for the period of performance.  If total material costs for all Level 2 work orders are projected to exceed $1,200,000 the Facilities Engineer must be immediately notified.  Subsequent notifications are required for every $25,000 thereafter.

Work orders greater than $50,000 require Program Manager and Contracting Officer approval prior work order issuance.

      - ISSUANCE OF WORK ORDERS. The Facilities Engineer will issue work orders during normal working hours. The Facilities Engineer may verbally order emergency work not to exceed $5,000.

    - WORK ORDER ACCOMPLISHMENT. The Facilities Engineer determines what tasks will be issued on a work order. The Contractor must accomplish each work order as issued by the Facilities Engineer IAW the has

applicable priority, response and completion time stated in Section 5.2.2.3.

      - PRIORITIES. There are five priorities for work orders. The Facilities Engineer will assign priorities when the work order is issued to the Contractor. The Government retains the right to upgrade or downgrade priorities of existing work orders. Such changes by the Government must not be arbitrary but must be used as necessary to ensure that ever- changing mission requirements are supported in a timely manner. The Contractor shall comply with Government established priorities.

        - PRIORITY 1 – EMERGENCY. Work that takes precedence over all other work and requires immediate action by the Contractor, including diverting personnel from other work to respond to the emergency. Usually, the work is necessary for the protection of health, safety, security of sensitive Government property, prevent damage to property or to meet an emergency operational requirement. Examples of emergency work include, but are not limited to:

- Loss of air conditioning or heating in any training space.

- Loss of electrical power to any training space.

- Natural gas leaks.

- Electrical problems that could lead to personal harm, damage to property, or result in a power failure affecting occupied buildings.

- Serious water leaks causing damage to property or interruption of service.

- Complete breakdown of refrigerators, cooking ranges or other primary kitchen equipment.

- Complete restriction in operation of plumbing fixtures or drain lines where no alternate facilities are available in the building.

- Door and lock repair were necessary to close buildings for security.

- Broken glass where it is necessary to close a building for security.

- Leaking roofs where damage to building contents may result.

- Problems arising from flooding of basements, crawl spaces or streets from stopped storm sewers or drains, etc.

- Problems arising from natural disasters, such as flash floods and storms.

- Failure of alarm systems.

- Protection from weather damage.

        - PRIORITY 2 – URGENT. Work that should be accomplished by the first available employee. Contractor personnel will normally not be diverted from other work to perform this work unless other specific response requirements dictate otherwise, such as P2 by COB. This includes work required to Correct a condition that could become an emergency, work that could seriously affect morale, work that has command emphasis, or work required by an authorized customer to accomplish its mission. Examples of urgent work include, but are not limited to:

- Minor electrical problems that will not lead to personal harm, damage to property, or result in a power failure affecting occupied buildings.

- Minor water leaks where no damage to property is likely to occur.

- Minor refrigeration problems where spoilage of food is not imminent.

- Providing shore tie connections for visiting vessels.

        - PRIORITY 3 – HIGH PRIORITY. Work that has an impact on morale or is priority due to mission requirements to meet command commitments. Work that does not require diversion of personnel from other work but should be completed before routine work. Examples of high priority work include, but are not limited to:

- Minor heating problems (not operating at full efficiency when weather is moderate).

- Repair door closer on interior door.

- Make new keys for door.

- Replace light bulbs in office where other bulbs provide light.

- Repair leaking faucet in restroom.

- Replace discolored ceiling tiles once the roof integrity or utility lines have been repaired.

        - PRIORITY 4 – ROUTINE. Work that does not meet the criteria of Priority 1, 2 or 3. Work in this category generally must be done in the most economical manner, on a first-come, first-served basis. These jobs include required work that, if not accomplished, would only continue an inconvenience or an unsightly condition. Examples of routine work include, but are not limited to:

- Install additional wall receptacle.

- Install new equipment.

        - PRIORITY 5 – DEFERRED. Work which must be accomplished and should be facilities Engineered but which may be more economically or logically accomplished later in conjunction with other work. This work may be accomplished as time permits. Examples of deferred work include, but are not limited to:

- Exterior painting during the winter months.

| Priority | Response, Begin Work | Completed |
| --- | --- | --- |
| 1 – Emergency | ASAP but no longer than 20 minutes (24 hours per day) | Sustained, continuous effort until emergencies are resolved (Priority may then be downgraded by the Facilities Engineer) |
| 2 – Urgent | n/a | Within 5 calendar days or as specified on the work order |
| 3 – High Priority | n/a | Within 20 calendar days or as specified on the work order |
| 4 – Routine | n/a | Within 45 calendar days or as specified in the work order |
| 5 – Deferred | n/a | Not to exceed 180 calendar days or as specified in the work order |

Note: Material delivery times do not relieve the Contractor from meeting the assigned prioritized timelines. The Facilities Engineer may at any time request the Contractor to provide evidence that any necessary parts have been ordered to complete a work order.

      - WORK ORDER DELAY NOTIFICATION. The Contractor shall immediately inform the Facilities Engineer when they cannot meet the above stated completion times on work orders issued with Priorities 2, 3, 4, and 5. This notification is for Government planning purposes only.

      - BACKLOG OF WORK. To facilitate maintenance management and to account for scheduling difficulties, it is normal and acceptable for facilities maintenance activities to carry a backlog of WORK ORDERS that have been issued but not yet accomplished.

      - BACKLOG REPORT. The Contractor shall submit a weekly backlog report. This report shall contain a complete listing of all open work orders including current charged costs.

    - LEVEL 3 – JOB ORDERS OVER $50,000.  If total cost for materials and/or subcontracted labor is in excess of $45,000, the work shall not be started without Contracting Officer and Program Manager written approval.  To request this approval, the Contractor submits a Job Cost Proposal via the Facilities Engineer and service work.  No work forecasted to exceed $45,000 in value shall be started without advance written approval.

  - CONTRACTOR WORK CONTROL.

    - CONTRACTOR WORK MANAGEMENT CENTER.

The Contractor shall operate and staff a work management center from 8:00 am to 5:00 pm during normal workdays. This center shall be the Contractor’s primary location for collecting and filing data, receiving, scheduling and recording work, and must serve as the primary office for the Contractor’s Project Manager and the designated point of contact during normal working hours. The following labor mix is anticipated:

- Engineering Management, may be senior Civil Engineer, Mechanical Engineer, or Engineering Manager

- Master Carpenter

- Locksmith

- Master Plumber

- Master Painter

- Journeyman Painter

- Master Electrician

- Master HVAC Technician

- Journeyman HVAC Technician

- Fire/Safety Officer

- 1.5 FTE Senior Maintenance Technicians familiar with campus

  - 2 individuals at 30 hours/week

- General Laborer

In addition to the base scope of work, these FTEs will be tasked with a variety of repair activities to be coordinated by the on-site command representatives. The Contractor is responsible for facilities maintenance management to include reception, scheduling, tracking, recording and processing of all preventive maintenance and work orders.

    - CONTRACTOR IDENTIFIED WORK. The Contractor shall implement and operate an inspection and work identification system. The Contractor is responsible for reporting all Contractor identified work to the Facilities Engineer. For all work identified, the Contractor shall submit a work order request. The Facilities Engineer will review the contractor-generated work order request and determine whether the request is to be approved, and if so, assign the priority, and issue the corresponding work order.

    - ANNUAL WORK PLAN FOR LEVEL 1 – PREVENTATIVE

MAINTENANCE WORK. The Contractor shall develop and submit a comprehensive annual work plan to the Facilities Engineer for review and approval within 60-days of start. This plan shall provide information as to when the Contractor will accomplish all Scheduled/Preventative Maintenance including but not limited to daily, monthly, quarterly, semiannual, annual, and biennial preventive maintenance (PM); annual overhauls, start-up and shut-down maintenance; and annual inspections for the equipment and facilities/services to be maintained under this contract, including: grounds maintenance, refuse collection, janitorial, pest control and custodial services. The Contractor shall use, as a minimum the current applicable year edition of RS MEANS as a recommended guide to develop the preventive maintenance section in the work plan. The Contractor shall implement the plan upon approval and make changes as submitted and approved by the Facilities Engineer.

    - MONTHLY WORK SCHEDULE. The Contractor shall develop, submit, and implement a monthly work schedule for all LEVEL 1 - Scheduled/Preventative Maintenance. These schedules must be submitted to the Facilities Engineer by the 15th day of the preceding month, showing the work to be completed during the subsequent month. The Contractor shall notify the Facilities Engineer in writing at least 2 working days prior to making any changes to the current monthly work schedule. This notification shall be made in writing and is subject to approval by the Facilities Engineer.

    - CORRECTIVE MAINTENANCE (CM) WORK ORDERS.  Contractor shall forward the original of the completed work order form to the Facilities Engineer within one working day after completion of the work order. A copy of the completed work order shall be retained by the Contractor. These requirements apply to all work. Invoices for material charged to work orders shall be filed by work order number. This information shall be available for review by the government at any time and shall become the property of the government at the completion of work performed.

    - POINT OF CONTACT FOR EMERGENCY WORK.  The Contractor shall provide the Facilities Engineer two points of contact with a telephone number to receive verbal assignment of Priority 1 – Emergency Work 24 hours a day, 7 days a week. During normal working hours this point of contact shall be available by contacting the Contractor’s Work Management Center. After normal working hours, the Contractor’s point of contact may be off-site, but the Contractor is still required to meet the response times for Emergency work. The Contractor shall furnish this information to the Facilities Engineer prior to contract start date and as changes occur. After normal working hours, the Contractor shall maintain a log of all calls received and action taken. Notification of after-hours work shall be made to the Facilities Engineer by 8:00 a.m. on the next working day.

    - MEETINGS. During the duration of contract performance, the Contractor shall attend a monthly scheduled meeting with the Facilities Engineer, Contracting Officer, Program Manager and other government representatives as needed to discuss any outstanding issues. At this meeting, the Contractor shall provide the Facilities Engineer with a written report listing any system/facility not functioning properly and the repair status including estimated repair date. The Contractor will be provided advance notice of any unscheduled meetings.

    - STATUS UPDATES. When requested verbally or in writing by the Facilities Engineer, the Contractor shall provide any facilities maintenance information (e.g., the status of any item of work, scheduling information, parts ordering and delivery information, etc.). Unless otherwise directed, the Contractor shall provide the requested information to the requestor within 1 hour.

    - RE-WORK. When directed by the Facilities Engineer, the contractor shall perform any work which was not performed or re-perform any work which was performed in an unsatisfactory manner. Unsatisfactory work includes, but is not limited to, work which is not performed IAW: specifications listed in this SOW; code requirements; manufacturer’s written specifications; etc. The response time and quality requirements as set forth in this contract must also apply to these rework actions. The Government may issue a Contract Discrepancy Report, and/or Performance Directive, if the Contractor fails to perform, or performs late, any work under this SOW.

    - PERFORMANCE DIRECTIVES. Performance directives (oral or written) may be issued by the Facilities Engineer, Contracting Officer, or other government officials authorized in writing by the Facilities Engineer to the contractor, and may include, but not be limited to, the following:

- To change the priority of an existing work order.

- To inform the Contractor of cancellation of a work order.

- To inform the Contractor of necessary re-work on unsatisfactory work.

- To inform the Contractor of meetings requiring attendance.

- To advise the Contractor of work requirements affected by other work being performed

- To modify the requirements of a work order.

The contractor shall respond in writing or electronic correspondence to a Performance Directive within 24 hours after receiving it unless directed otherwise.

  - WORK RECORDING AND FILING.

    - PROJECT FILES. A separate project folder shall be maintained for each Job Order with a combined material and/or subcontracted labor cost greater than $5,000. The Contractor shall maintain complete and accurate records of all materials (including copies of receipts) and labor categories and hours used. This information shall be available for review by the Government at any time and shall become the property of the Government at the completion of each contract option year for work performed during that year or termination of the contract, whichever comes first.

    - MARK-UP DRAWINGS. The Contractor shall provide mark-up drawings or other information for updating record drawings when any change is made as part of this contract to a facility, system, equipment or unknown interferences or utilities are discovered. Mark-up drawings shall be current, legible, and include, in detail, any update resulting from Contractor performed work. All Contractor changes to drawings shall be made in red ink. This documentation is required whenever an alteration or reconfiguration of an existing system is made. The Contractor shall ensure that drawings are annotated within one week of completing the construction or alteration. The annotated drawings shall be submitted to the Government for updating the master drawings.

    - EQUIPMENT RENTALS. Equipment costs when incurred shall be based on actual vendor rental rates in the local area. If vendor rates cannot be easily found, then RS Means, rental catalogs or other verifiable standards may be acceptable.  Note: Government-owned equipment shall be used first if available, followed by contractor-owned equipment, with rental equipment being the last option. Non-availability of government or rental equipment is not acceptable justification for late or unsatisfactory performance.  Equipment rental costs shall be included in material and subcontracted labor cost tracking.  No equipment rentals shall be made without prior approval from the Facilities Engineer.

    - STAFFING AND PERFORMANCE. The contractor shall provide at minimum the staff identified in 4.3.1.  Staffing shall be completed within 90 days.  If particular trades or expertise cannot be realized within the area, the Contractor may submit a staffing alteration request.  The alteration request shall receive written approval from the Facilities Engineer prior to onboarding.

  - PERFORMANCE OF WORK.

    - FACTORS AFFECTING CONTRACTOR PERFORMANCE. The Contractor shall notify the Facilities Engineer of any circumstances of needed repair of the facilities, unusual soiling of an area which may affect performance of contract work, unhealthy or hazardous conditions, or any delays or interference of work caused by individuals not employed by the Contractor. Such reports shall be made as expeditiously as possible. The Contractor shall report to the Facilities Engineer other circumstances which affect performance of the work required under this contract. In any event, the report shall be made not later than close of business on the same day.

    - LOST AND FOUND. The Contractor shall report to Security all personal articles or other property found by Contractor’s employees. Found property shall be turned into the Security Office by the Contractor within 1 working day.

    - INSTALLED BUILDING EQUIPMENT REPLACEMENT.  If an item of installed building equipment is determined by the Contractor to be beyond economical repair, the Contractor shall recommend to the Facilities Engineer that such installed building equipment should be replaced. Substantiating data to support the recommendation shall be provided. If the Government determines that such equipment should be replaced or repaired, the Facilities Engineer will issue a corresponding work order.  The Contractor shall not replace building equipment without prior authorization.

      - DOCUMENTATION. The Contractor shall provide justification documents with recommendations to purchase new and replacement equipment. The Contractor’s justification shall include the following minimum information:

- The cost of repairing parts.

- The replacement cost and availability.

- The rationale for replacement rather than repair.

- A statement that the replacement equipment will fit into the available space, perform the required function and operate on available installed utility services.

- Photographs of existing equipment.

      - SALVAGE. The Government retains all salvage rights to replace property of value. The Government will determine property value. If an item is determined to be of no value, the Contractor shall dispose of it as directed by the Facilities Engineer. The contractor shall not dispose of any property of value until it receives notification from the Facilities Engineer.

CONTRACT EMPLOYEES ARE FORBIDDEN TO REMOVE ANY GOVERNMENT- OWNED PROPERTY OR MATERIAL; VIOLATORS WILL BE PROSECUTED TO THE FULL EXTENT OF THE LAW.

    - DIGGING OPERATIONS. The Contractor shall review all construction plans (including those of other government contractors) involving digging operations and locate and stake out underground utility pipes/cables prior to commencement of excavation. The Contractor shall obtain a drawing indicating the area affected. The Contractor shall verify the location of all utilities, abandoned or active. The ground must be marked in an appropriate color for each utility. Following the excavation the drawing must be returned to the government, marked up indicating any difference between the drawing and the actual conditions. All marks must be made in red ink. The Contractor may be required to excavate in order to verify actual location of some utilities. The Contractor shall coordinate with Coast Guard personnel concerning the location of telephone cables.

    - CONTRACTOR DIGGING OPERATIONS. Should the Contractor need to perform sub-surface work, they shall submit an excavation permit to the Facilities Engineer, 7 days prior to commencement of operations. Using whatever means necessary, the Contractor shall verify the location of all existing buried utilities prior to submitting the completed digging permit and must meet with the Facilities Engineer or their designated representative at the work site prior to excavating. Where it appears that excavation will either cross or come within the vicinity of an existing utility line, the contractor must excavate with hand tools to locate the buried utility. Once exposed, the utility must be protected from damage. For verification of utility locations, no method of excavation other than hand tools or vacuum potholing will be permitted.

    - MATERIAL SUBSTITUTION.  The Contractor shall submit all requests for building material substitutions to the Facilities Engineer. Each request shall include specific identification of the proposed substitute; justification for the necessity of the substitution, certified test reports of the proposed substitute, including all tests required by the specification for the substitute material.

    - MATCHING EXISTING.  The Contractor shall match the existing condition unless otherwise noted.

    - APPEARANCE. Colors, textures, patterns, or any other appearance characteristics for paint, plastic laminate, floor coverings, wall coverings, ceramic tile, quarry tile, wood, asphalt shingles, sealants, toilet fixtures, lavatories, showers, bathtubs, water closets, or any other materials, etc., used in all work under this contract shall be approved by the Facilities Engineer.

    - SIZE. Where new work is adjacent, contiguous, or must be incorporated/ installed with or into existing work, the Contractor shall provide material that matches the existing size, and condition. Where new carpentry work, including but not limited to, studs, joists, plates, rafters, trims, stops, jambs, frames, sills, bases, mullions, fascia’s, curbs, bracings, etc., is adjacent or contiguous to existing work, new members must be modified, if required, to assure similar sizes and provide for surface continuity and uniformity of surface with the existing condition. New work must be modified by reducing larger members to small sizes or by increasing the size of smaller members by the addition of fillers (3/4 inches maximum), as applicable. Where new piping must be incorporated with an existing system consisting of nonstandard piping sizes, the Contractor shall machine fabricate unions, adapters, sleeves, etc., as required to assure incorporation of the new piping work.

    - MANUFACTURER’S  TECHNICAL REPRESENTATIVE.  The Contractor shall obtain the services of the factory technical representative as part of this contract whenever the complexity or specialty of the work requires such consultation or is requested by the Facilities Engineer by work order. The Contractor shall inform the Facilities Engineer prior to obtaining the services of a technical representative in all cases. The Contractor shall perform the Corrective work IAW the factory representative’s recommendations, unless otherwise directed. Reimbursement by the government for the technical representative’s services is subject to Facilities Engineer approval.  These costs shall be included in total combined work for materials and/or subcontracted labor.

    - MANUFACTURER’S INSTRUCTIONS. Manufacturer’s instructions and wiring diagrams, including technical data, will be provided when available for the Contractor’s use and information. Contractor shall perform diagnostics/trouble shooting of equipment as required to perform the work requested without benefit of manufacturer’s instructions and wiring diagrams if such information is not available. Non-availability of manufacturer’s instructions and wiring diagrams must not be used as a basis for delays, defective work, etc. The Contractor may obtain instructions and diagrams from the equipment manufacturer at no additional cost to the Government.  If costs will be incurred, advance approval from the Facilities Engineer is required.

    - BUILDING AND SITE SECURITY. Where existing doors, windows or other exterior or interior surfaces are removed, the Contractor shall provide temporary closures to secure the building when work is not being performed and to provide protection from the weather. Temporary closure must be plywood, ½-inch minimum with 2 x 4 framing, and must completely cover the opening in the surface, and must be secured in place in a rigid, firm, and substantial manner. Where openings are made in existing fences, such as fabric or gate removal, the Contractor shall, similarly, cover the opening with similar types of existing fencing material. Prior to the start of facility or site work, the Contractor must isolate and secure the work area with ropes, rope stands, signs, or other barriers to prevent entry by unauthorized personnel. After normal work hours, the contractor must notify security of any temporary closures.  Security must adjust rounds to ensure proper monitoring of any penetrations.

    - BUILDING SECURITY. The Contractor is responsible for turning off all lights and locking all interior and exterior doors after the completion of janitorial services each day except where authorized Coast Guard personnel are using the specific space.

    - DAMAGE

    - CONTRACTOR-CAUSED DAMAGE TO PERSONAL PROPERTY.

The Contractor shall promptly repair or replace any Contractor-caused damage to personal property at no expense to the Government or personal property owner.

    - CONTRACTOR-CAUSED DAMAGE   TO   GOVERNMENT PROPERTY. The Contractor shall repair or replace any Contractor-caused damage (due to negligence, incompetence, failure to use reasonable care, etc.,) to Government property (facilities, vehicles, vessels, equipment (including installed building equipment), materials, supplies, and grounds) at no additional expense to the Government as directed by the Facilities Engineer. When a defect or deficiency in the services performed or materials furnished by the Contractor results in damage to Government property, the Contractor is liable for costs to repair the damage. This paragraph does not limit the Government’s rights inherent in contract clauses listed elsewhere in this contract.

    - CONTRACTOR CLEANUP. The Contractor shall always keep all work areas free from accumulated waste material, refuse, tools, scaffolding, equipment, and materials. Upon securing the area, the Contractor shall leave the work and premises in a clean, neat, and workmanlike condition. At the conclusion of work, cleanup includes necessary dusting, vacuuming, wiping down all surfaces as necessary to remove dust, dirt or other marks.

    - QUALITY OF WORK. The quality of work accomplished, and the materials used must meet all standards specified in this SOW. All services/work shall be performed IAW applicable national codes, Federal, State and Local regulations, and manufacturers’ recommendations.

    - CODE REQUIREMENTS. The Contractor shall perform all facilities maintenance activities and other work relating to planning, alteration, installation of new equipment, repair and construction of real property, including utilities generation and utilities distribution systems in conformance to the latest version of the documents listed and referenced in this SOW. If reference documents have different standards, the most conservative standard will govern. The Contractor is responsible for obtaining the necessary professional services to ensure compliance. Where the standard or code refers to local jurisdiction, this must mean Chief, Facilities Engineering Division (FE).

- IBC: International Building Code

- NFPA: National Fire Protection Association Codes and Standards

- 29 CFR 1910 119(k)

- National Life Safety Code

- NEC: National Electric Code

- International Mechanical Code

- ASME Safety Code for Elevator and Escalators

- ASHRAE

- VDOT

- OSHA

- COE EM 385 1-1 Safety and Health Requirement Manual

- All other National, State and Local code requirements

# SPECIFIC TASKS.

The order of these specific tasks is not an indication of the priority or importance of the task.

  - SEWER SYSTEMS (SANITARY & STORMWATER).

SCOPE. The Contractor shall inspect, test, maintain, alter, repair, replace, construct, and install new sections of the sanitary and storm sewer collection and associated systems. These systems shall be kept in fully operational condition. The systems include all sewer lines, catch basins, filters boxes, catchment basins/BMPs, manholes, lift stations, monitoring equipment, irrigation piping, pumps, compressors, grease traps, lift stations, and other related equipment. Portions of the sewer system are considered permit-required confined spaces and operations in those spaces must be conducted IAW the contractor’s Confined Space Entry Program contained in the contractor’s approved Safety Plan.

    - SCHEDULED/PREVENTATIVE MAINTENANCE AND OPERATION.

      - PREVENTIVE MAINTENANCE. The Contractor shall perform preventive maintenance including controlling tree roots in sewer and storm drains; cleaning sewer lines with cutting equipment; monthly treatment of urinals for urine salt build-up; keeping building and drainage pipes/ditches clear of debris for proper rainwater runoff; exercising all water main isolation valves annually; pond vegetation treatment/control; including all required inspections, IAW the Contractor’s Annual Work Plan at the frequencies specified in RS MEANS.

LEVEL 2 – WORK ORDERS.  The Contractor shall perform service work on all sewer mains, service lines, lift stations, pumps, manholes, internal plumbing systems, and associated equipment when ordered on an approved work order. The quality of work accomplished must meet manufacturer’s specifications, applicable documents, and all requirements of this SOW.

      - REPAIRS. This work includes repair, alteration, replacement or installation of all system components. When a malfunction in the system such as stoppages, structural failures, overloading, mechanical failures, electrical failures, etc., occurs, the Contractor must locate the cause and Correct the problem.

  - ELECTRICAL SYSTEMS.

SCOPE. The Contractor shall inspect, test, operate, maintain, alter, troubleshoot, repair, replace, and install electrical systems. All electrical systems included within buildings located on the former Birmingham-Southern College campus are within the realm of work required under this contract. The Contractor may also be required to install new additions to existing electrical systems. The systems, including emergency generators, emergency lighting systems, fire alarms systems, interior building wiring systems, and exterior wiring systems must be operated and maintained to provide that all critical system reliability rates and all specified standards are met or exceeded.

SYSTEM OUTAGES. The Contractor shall submit a Utility Outage Request Form for approval 14 days prior to closing any facility or part of a facility for work required to be performed. The Contractor shall attend planning meetings that may affect the power systems the Contractor operates and maintains.

CODE COMPLIANCE. All electrical work shall be performed in strict accordance with the National Electric Code, Life Safety Standards of the National Fire Code, National Fire Protection Association, and the Coast Guard Civil Engineering Manual. All high voltage work must be performed by fully qualified high voltage electricians. The NEC states that any voltage above 600 volts is considered high voltage. All elevator inspections, test, adjustments, maintenance, alterations, repairs and replacements must conform to the latest editions and supplements of the ASME Safety Code for Elevators. The Contractor shall ensure that proposed furnished materials conform to the standards of the appropriate testing organization and maintain a file of proof of such determinations. This file must be available for Facilities Engineer inspection upon request. The label of the testing organization must be accepted as proof of conforming to this requirement. In lieu of the label, the Contractor may obtain a written certification from any nationally recognized testing agency, adequately equipped and competent to perform such services, that the item has been tested and conforms to the standards, including methods of test, of the above testing organization. The file must be available to the Facilities Engineer upon request and turned over to the Government at the end of the contract.

CRITICAL SYSTEM RELIABILITY. Building systems and related equipment designated as critical by the Government are noted below. The Contractor shall provide maintenance support and spare parts inventory to ensure continuous operation of all fire alarms and fire suppression systems.  Repairs shall be started within 2 hours of notification of failure.

      - ALARM SYSTEMS. The Contractor shall inspect, test, operate, and maintain all fire detection and fire suppression alarm components, associated control panels, and monitoring equipment, including all communication lines connecting the systems including the Monaco system. The Contractor shall perform all work IAW the NFPA Codes, NICET and equipment manufacturer instructions. The Contractor shall notify the Facilities Engineer in writing 72 hours prior to performing any maintenance or testing of fire or sprinkler alarms.

        - INSPECTIONS AND TESTING. The Contractor shall perform all alarm inspections and tests during normal working hours, unless otherwise approved in advance. Test all devices so the interval between tests on a specific device is not less than 1 year. All devices within a single building must be inspected and tested within a single two-week period. The Contractor shall provide a written report to the Facilities Engineer within 2 working days following the conclusion of the tests indicating the results. The report must include (as a minimum) the date, location and description of system and components tested, discrepancies noted, and Corrective action required.

        - PROBLEM ALARM SYSTEMS. If any test reveals a weakness in the degree of security provided by an alarm system, or if any evidence is found that tampering with equipment or connecting lines, switches, detectors, or other sensitive

elements have occurred; that any adjustment has been changed; or that any equipment or sensitive element has been moved or removed; the Contractor shall immediately report this condition to the Facilities Engineer. If any of the aforementioned problems occur, the Contractor shall be responsible for obtaining technical representative assistance in trouble-shooting the affected system.

LEVEL 2 – WORK ORDERS. The Contractor shall perform service work on all electrical systems, and associated components when ordered on a Facilities Engineer approved Work Order. The quality of work accomplished must be IAW all federal, state, local, and USCG requirements and meet manufacturers’ specifications and the contractor’s Quality Control Plan.

      - INTERIOR ELECTRICAL WORK. The Contractor shall maintain, repair, replace, alter, procure, and install new or additional interior electrical system components. This work includes, but is not limited to, disconnect devices, cables, wires, raceways, ducts, capacitors, regulators, grounding equipment, wall switches, conduit, receptacles, fire and smoke alarms, installed lighting fixtures, lamps and clock systems, and any other parts and accessories necessary to distribute the electricity to the using equipment.

      - EXTERIOR ELECTRICAL WORK. The Contractor shall maintain, repair, replace, alter, procure, and install new or additional exterior electrical system components. This work includes but is not limited to disconnect devices, cables, wires, ducts, grounding equipment, conduit, receptacles, fire alarms, installed lighting fixtures, lamps, and any other parts and accessories necessary to distribute electricity to the using equipment. Materials must comply with applicable Federal specifications and be comparable to the original construction quality for the building or unit and must be made in such a manner as to ensure a safe and reliable electrical system. Exterior electrical work includes, but is not limited to:

        - HIGH VOLTAGE DISTRIBUTION. The Contractor shall be responsible for high voltage repairs, splices, inspection, operation of sectionalizing switches, etc., in case of power outages.

  - HVACR SYSTEMS.

SCOPE. The Contractor shall operate, inspect, test, maintain, alter, procure and install, remove, repair, replace, and construct as necessary, all Heating, Ventilation, Air Conditioning, and refrigeration equipment, fuel systems, and associated components and control systems.  The terms heating, ventilation, and air conditioning include all such equipment, regardless of size and capacity. The Contractor shall employ qualified and licensed service personnel to perform all work, service and repairs IAW Federal, State and Local requirements. All repairs must be made in compliance with good workmanship standards and IAW manufacturer’s specifications and recommended procedures.

OPERATING AND MAINTENANCE. The Contractor shall be responsible for maintaining complete control of the operation and maintenance of the heating, ventilation, and air conditioning systems including: start-up and shutdown, operator maintenance, inspection of heating sources, fuel storage and handling, feed water, condensing, air system equipment, air conditioning equipment, ventilation equipment, miscellaneous pumps and plant instrumentation, and electrical equipment and components, as well as items external to the HVAC system buildings. The Contractor shall be responsible for maintaining complete control of the HVAC system operation by preparation of and adherence to written operating procedures.

PARTS. Only manufacturers’ approved replacement parts and lubricants shall be used. All parts supplied under this specification must be 100% compatible with the existing hardware and software as configured and installed. Air filters must be MERV-8 pleated, rated for CFM equipment, and dated when installed. Dedicated Outside Air Units (DOAS), ERV’s and 100% outside air make-up units may require more frequent filter changes. For estimating purposes, monthly filter changes must be planned for these specific units. The Contractor shall maintain an inventory of items to service this contract in the specified time frames.

CFC & HCFC HANDLING. The Contractor shall comply with all regulations concerning the use, handling, documentation, and disposal of CFCs and HCFCs, boiler chemicals, and other hazardous or toxic substances.

LEVEL 1 - SCHEDULED/PREVENTATIVE MAINTENANCE AND OPERATION.

      - PREVENTIVE MAINTENANCE. The Contractor shall schedule and perform preventative maintenance on systems and equipment. Preventive Maintenance Records must be maintained and kept up to date. The Contractor’s work must be accomplished IAW applicable codes, manufacturer’s instructions and recommendations, and the Quality Control Program.

        - GENERAL. This work specifically includes recordkeeping of operations and conditions; analysis of records to Correct sub-optimal practices; water treatment; monitoring warranties; testing operations and efficiencies of boilers; periodic operation and inspection of idle equipment; periodic testing and certification; annual overhauls; and cleaning, preservation, lubrication, and adjustment of plant equipment. Seasonal start up and shutdown of all heating and cooling systems. Operating logs must be maintained on all equipment as specified. The systems must be maintained free from defect and damage; no components must be missing; all parts must be tight; and the components must operate as designed. All parts must be lubricated, and all fluids must be maintained at required levels. This includes but is not limited to, inspecting and lubricating such components as air compressors, valve packing glands, dampers, bearings, linkages, switches directly pertaining to the control system, replacing valve packing materials on valves to prevent leaking; examining, adjusting, calibrating and cleaning all thermostats, humidity controls, pressure controls, valves, relays, motors and accessories to the control systems; and stroking all isolation valves annually. The Contractor shall be responsible for submitting work order request for Corrective actions necessary to accomplish any deficiency identified during the PM.

        - PLANNED SERVICE OUTAGE. When maintenance, inspection or repairs require a discontinuance or reduction in a HVAC systems operation, the Contractor shall coordinate with the Facilities Engineer prior to outage.

WATER AND GLYCOL SOLUTION TESTING AND TREATMENT.

The Contractor shall collect feed water, boiler water and condensate samples from each operating boiler for testing. Chiller water and Cooling Tower water testing must be conducted monthly when the equipment is operational during the cooling season. The Contractor shall perform the necessary tests to meet applicable manufacturer requirements or local requirements on pH and total dissolved solids and record the test results in a log. A water sample analysis report must be forwarded by the 10th day of each month to the Facilities Engineer. This report must also include the parameters used for determining the acceptable conditions. The Contractor shall provide all water treatment chemicals required for plant operations.

      - CALIBRATION. The Contractor shall test all pressure and temperature gauges annually, attach a self-adhesive seal on each gauge certifying that it has been calibrated. The date of the calibration and the initials of the person performing the calibration must be noted on the sticker. The gauges must be calibrated using a standard dead weight tester or a calibrated master gauge or other procedure acceptable to the Facilities Engineer. The Contractor’s procedures for calibrating gauges shall be made as part of their approved boiler operating procedures.

BOILER SYSTEMS STANDARDS.

      - BOILER OPERATING PROCEDURES. The contractor is fully responsible for the safe operation and maintenance of all boilers and related equipment IAW Federal, State, Local, Coast Guard, and manufacturer written instructions and requirements. If failure to do so leads to damage, the contractor is fully responsible for repairs and replacement, including temporary boilers or related equipment at no additional cost to the Government.

        - PROCEDURES. Work affecting the structural or pressure integrity of the boiler must be performed by the contractor only when directed by the Facilities Engineer and IAW written procedures approved by the Facilities Engineer.  Completed work will be inspected by the Facilities Engineer prior to returning the affected unit to operation.

        - COMBUSTION EFFICIENCY. The contractor shall conduct annual combustion efficiency testing and adjustment on all boilers IAW manufacturer specifications and recommendations.

      - MECHANICAL ROOM INSPECTIONS. The Contractor shall conduct an operational inspection of all boilers mechanical rooms at TRACEN Birmingham every day and document the results of this inspection in the operating log. These inspections must be performed by a HVAC Technician and may include minor general cleaning. Work order requests should be generated for any discrepancies noted during the inspection.

    - LEVEL 2 – WORK ORDERS. The Contractor shall perform service work on all heating systems, boilers, control systems, unfired pressure vessels, chillers, air conditioners, fan coil units, unit heaters, heat pumps, ventilation systems, fuel systems and associated components when ordered on a Facilities Engineer approved Work Order.  The quality of work accomplished must be IAW all federal, state, local, and USCG requirements and meet manufacturers’ specifications and the contractor’s Quality Control Plan.

      - CODE COMPLIANCE. The Contractor shall maintain and repair all boilers and furnaces used in the production of domestic heat and domestic hot water and all distribution systems IAW the American Society of Mechanical Engineers code and OSHA standards and requirements at a minimum.

  - WATER DISTRIBUTION AND FIRE SUPPRESSION SYSTEMS.

SCOPE. The Contractor shall operate, inspect, test, maintain, alter, procure and install, remove, repair, replace, and construct as necessary the potable water storage, distribution, and fire suppression systems to ensure a fully operational condition. The system includes all supply mains, booster pumps and controls, storage tanks, distribution lines, service lines, hydrants, fire department connections, valves, irrigation sprinkler systems, fire protection systems, and meters as described below.

    - LEVEL 1 - SCHEDULED/PREVENTATIVE MAINTENANCE AND OPERATION.

      - PREVENTIVE MAINTENANCE. The Contractor shall schedule and perform preventative maintenance on systems and equipment according to frequencies recommended in RS MEANS, original equipment manufacturer manuals, Facilities Maintenance & Repair Cost Data, current year and IAW the Annual Work Plan. Preventive Maintenance Records must be maintained and kept up to date. The Contractor’s work shall be accomplished IAW applicable codes, manufacturer’s instructions and recommendations, and the Quality Control Program.

        - HYDRANT FLUSHING. All fire hydrants and dead ends must be flushed and flow tested once each year in the spring IAW NFPA 291 and the results entered on the required forms. These forms must be available for inspection by the FACILITIES ENGINEER when requested.

        - OUT OF COMMISSION HYDRANTS. All hydrants which are found to be inoperative or temporarily taken out of service must be tagged out and reported immediately to the Facilities Engineer.

        - BACKFLOW PREVENTERS. The Contractor shall annually inspect and test all backflow preventers on the potable water system. Evidence of certification of personnel conducting tests must be submitted for approval to the Facilities Engineer. The Contractor shall test backflow preventers IAW the State of Alabama requirements and submit annual test results by 1 January.

        - FIRE PROTECTION SPRINKLER SYSTEM TESTING.  The Contractor shall meet the maintenance and testing requirements of the latest edition of NFPA 25 entitled “Inspection, testing and maintenance of water-based Fire Protection systems”. The Contractor shall submit a written report similar to NFPA 25 Annex B to the Facilities Engineer, as required by NFPA 25.

    - LEVEL 2 – WORK ORDERS. The Contractor shall perform service work when ordered on an approved work order. The quality of work accomplished must be IAW all federal, state, local, and USCG requirements and meet manufacturers’ specifications and the contractor’s Quality Control Plan.

      - REPAIRS. This work includes repair, alteration, replacement or installation of all system components. The Contractor shall locate the cause and correct the problem. These may include the installation of new parts as required, including repairs of broken water mains, joint leaks, broken service lines, or damaged fire hydrants. All existing mains repaired or opened must be disinfected and flushed IAW AWWA Standard C601- 68.

  - BUILDINGS AND STRUCTURES.

SCOPE. The Contractor shall operate, inspect, test, maintain, alter, procure and install, remove, repair, replace, and construct as necessary all buildings on the former Birmingham-Southern College campus.  All work must be performed IAW applicable National codes, and all Federal, State and Local laws. Maintenance, repair, installation, and alteration of buildings and structures includes, but is not limited to, work on: foundations, walls, doors, windows, roofing, floors and floor coverings, porches, balconies, patios, stairs, fixtures and hardware, exterior and interior painting, glazing, roofing, interior plumbing, interior rough and finish carpentry, miscellaneous carpentry, elevators, structural systems and other equipment affixed and installed as part of the building. This requirement also includes fencing, flag poles, grease racks, wash racks, training aides, monuments, bleachers, picnic tables, park benches, huts, sidewalks, placement of concrete, platforms, fire ladders, interior woodwork trim, identification signs and/or plaques and picture frames, cabinets, partitions, furniture, ceilings, duct work, radiators, grills, dampers, exterior carpentry, and other miscellaneous structures.

5.5.1 LEVEL 1 - SCHEDULED/PREVENTATIVE MAINTENANCE AND OPERATION.

      - PREVENTIVE MAINTENANCE. The Contractor shall schedule and perform preventative maintenance on facilities, systems, and equipment according to frequencies recommended in RS MEANS, original equipment manufacturer manuals, Facilities Maintenance & Repair Cost Data, current year and IAW the Annual Work Plan. Preventive Maintenance Records must be maintained and kept up to date. The Contractor’s work shall be accomplished IAW applicable codes, manufacturer’s instructions and recommendations, and the Quality Control Program.

      - FACILITIES INSPECTION PLAN. The Contractor shall inspect all buildings and structures on an annual basis. The Contractor must develop an annual Facilities Inspection Plan and incorporate it into their Annual Work Plan which is due with the proposal and updated annually when the contract option year is exercised. As a minimum, the plan must include the inspection of those items identified in the Coast Guard COMDTINST M11000.11(series). A copy of the inspection report must be submitted to the FACILITIES ENGINEER within 5 days of completion of each inspection. All Contractor identified work order requests must be submitted with the report.

      - ROOFING INSPECTION REPORT. The Contractor shall record inspection results and location of deficiencies in an annual report which must include deficiencies noted, the severity, and recommended Corrective action. The Contractor shall maintain this report on file and provide a copy of the report to the Facilities Engineer within 10 days of completion of each inspection. Inspections must be conducted IAW with the roof warranty requirements, the latest NRCA, Roofing and Waterproofing Manual, the SMACNA and the Architectural Sheet Metal Manual. All contractor identified work order requests must be submitted with the report.

      - PAINT RECORDS. The Contractor shall maintain a painting log containing specifics on paint type and color used (including self-help), method of application, and gallons used for each interior compartment or room, and for building exteriors. Make it available to the Facilities Engineer upon request and turn over to the Government at completion.

    - LEVEL 2 – WORK ORDERS. The Contractor shall perform service work when ordered on an approved work order. The quality of work accomplished must be IAW all federal, state, local, and USCG requirements and meet manufacturers’ specifications and the contractor’s Quality Control Plan.

      - METAL WORKING. The Contractor shall maintain, repair, replace, fabricate, procure, and install all types of metal and alloy parts and components of buildings and structures, install building equipment, food service and kitchen equipment, and install metal components in support of other maintenance activities. Metal working includes heating and bending metal to form shapes; drilling, torch cutting, hammer forging, grinding, sawing and fitting of metal parts. The Contractor must weld all types of metals using electric, acetylene and/or inert gas shielded welding processes. Welding will be performed on light, heavy gauge, and hardened metals using flat, vertical, horizontal, and overhead positions, processes include preheating, brazing, bead welding, tack welding, flame cutting, pressure welding, and heat treating. Metal working includes the full range of metal working and sheet metal activities such as:

      - PAINTING. The Contractor shall provide painting services including surface preparation, mixing and application of coatings applied to all buildings, structures, facilities and all government systems located on the Training Center. The quality of coating must be IAW the Coast Guard Color and Coating Manual. This work also includes refinishing wood floors, exterior stripping and marking, applying and removing wallpaper and other decorative wall coverings; and stenciling. All work must be performed IAW manufacturers written recommendations for the type of material, atmospheric conditions and proposed use of the item(s) being painted.

        - SURFACE PAINT PROTECTION. The Contractor shall place drop cloths and other protective coverings on landscaping, surrounding areas and structures, furnishings, walls, trim, and floors, as required; move and replace furnishings and fixtures; remove paint spots, spills, etc., from areas to remain unpainted; and clean up and remove all dust and debris from the work sites.

        - BARRIERS AND SIGNS. When working in public areas, the Contractor shall provide suitable barriers and signs posted at all entrances of areas in which painting is being accomplished. “WET PAINT” signs must be posted where applicable.

        - PAINTING MATERIALS. Paints shall be stored in sealed containers that plainly show the designated name, formula, or specification number, batch number, color, date of manufacture, manufacturer’s directions, and nature of manufacturer, all of which must be plainly legible at the time of use. Pigmented paint must be furnished in containers not larger than 5 gallons. The use of paint containing lead is strictly prohibited. USCG and EPA encourage the use of low VOC paint materials. Upon request from the Facilities Engineer, the Contractor shall furnish the manufacturers’ recommendations for surface preparation, application and use for all material proposed.

- COLOR CHARTS. The Coast Guard utilizes a set of standard colors.

- APPROVAL OF MATERIAL. All deviations from standard paints must be approved by the Facilities Engineer prior to purchase and use.

- VOLATILE ORGANIC COMPOUND (VOC) COMPLIANCE.

- The Contractor must comply with local VOC regulations. The contractor shall submit an acceptable VOC compliance plan to the Facilities Engineer for review and approval 30 days after contract start date.

- PREPARATION OF SURFACES. All patching, sanding, cleaning and other surface preparation must be done in strict accordance with the manufacturers’ recommendations. The contractor shall inspect surfaces after preparation and receive Facilities Engineer approval before application of any coatings.

- APPLICATION OF PAINT. The Contractor shall use commercially accepted methods and manufacturer’s recommendations concerning application tools, temperature, humidity, wind velocity, dust free conditions, etc., when applying paint. Each coat shall be prepared IAW the paint manufacturer’s recommendations before the next coat is applied. Each coat must be smooth and free from runs, sags, brush or roller edge marks or other surface preparation defects. Paint surfaces adjoining other materials or colors must be sharp and clean without overlapping. Once new coatings are completely dry, windows that are stuck from being painted must be freed up to ensure ease of opening and closing. Painted surfaces must blend or match the color and surface of surrounding areas as required.

        - CLEAN-UP. The Contractor shall leave the premises in a neat and orderly condition at the close of each day’s work. Ladders, drop cloths and other equipment must be neatly stacked in an area away from doors and windows. Paint containers must be securely closed. Flammable items and waste must be removed from the premises. Items removed or masked for protection must be replaced in original position or masking removed. Upon completion of work, ladders, containers, tools, equipment, surplus materials and debris must be removed from the site and the premises must be left in a clean and undamaged condition. Floors and other surfaces not having been painted must be left in a splatter, dirt, and dust-free condition.

      - CARPENTRY AND MASONRY.

        - CARPENTRY. The Contractor shall perform all carpentry work necessary to maintain all buildings and structures at commercial standards. The Contractor’s work shall be planned and accomplished to offer maximum resistance to fungus, mildew, termites, water absorption and all other harmful effects caused by the environment. All wood provided and installed by the Contractor, in contact with concrete and masonry, must be preserved and treated by pressure methods and marked IAW the American Wood Preservers Institute Standards. Wood treated with waterborne preservatives must be air and kiln dried to the moisture content IAW industry standards for lumber and marked with the word “dry”. Treated wood must be used in all exposed locations that lack protection from the weather. If a cut is made in treated wood, the cut must be brush coated with a wood preservative. All carpentry work performed must be consistent with the construction and appearance of the existing building or structure. All species of wood for interior and exterior work will be utilized during this contract and will be specified in individual service work orders. The Contractor’s work includes but is not limited to the following tasks:

- GLASS. Glass replacement shall be the same type, size, and quality as the original. The size of glass windows which may need replacing are normally standard sizes and generally stocked; however, the actual size must be determined at the time of replacement and the glass cut facilities Engineer. Cracked or broken glass must be removed and disposed of by the contractor. Glazing compound or sealant must be removed. Damaged or deteriorated sashes, frames, and other components must be removed and replaced. Misaligned frames must be realigned and made plumb. The replacement glass must be installed on the same day, if possible, the damaged glass is removed. If this is not possible, the contractor must completely close and seal the window opening with ½-inch plywood. Plywood must be secured on the exterior and must be mounted to deflect rain from the building. Temporary enclosures are subject to approval by Facilities Engineer.

- FRAMES. Frames damaged or warped beyond economic repair shall be reported to the Facilities Engineer. The contractor must clean and prime metal frames prior to glazing. The contractor must sand and seal wood frames. Wood frames, including rabbets, must be primed before glazing compound or sealant is applied. The contractor must realign frames and make plumbs before glazing installation. The contractor must thoroughly clean glass surfaces and remove labels, paint spots, putty, and other defacements. As the work is completed, all debris must be removed from the job site.

- DOORS. Procure and install, replace or repair doors, door frames, sills, trim and casings, locksets, hardware, closures, fillings and similar items.

- GENERAL. Fabricate or repair wooden items such as cabinets, plaques, furniture, doors (including decorative doors), windows, shelves, picture frames including glass if applicable, shipping crates for shipment of Government equipment/materials including training aides, and tables/stands/other related components for training aides, etc. Procure and install securing devices to

modify or repair structures using fasteners such as screws, glue, dowels, stays, metal ties, blocks, braces, cleats, bolts, nails, or staples. Procure and install, repair or replace fencing. Procure and install, repair or replace fiberglass insulation. Perform other similar or related repairs. Repair and relocate systems furniture.

        - MASONRY, PLASTER, AND CONCRETE. The Contractor shall perform all masonry and concrete work necessary to maintain all facilities on the former Birmingham-Southern College campus. The Contractor shall plan, layout, mix, apply and finish the plaster work on surfaces such as drywall, metal lath, concrete, and rock lath. This work is performed on interior and exterior walls and ceilings. The Contractor shall build forms for, place, spread, level and finish such items as concrete walks, curbing, concrete pads for industrial equipment and machinery, construct manholes, and duct work.

      - ROOFING AND ROOFING ACCESSORIES.  The Contractor shall perform roof repair and replacement of roof accessories, such as flashing, gutters, downspouts, ventilators, valleys, and parapet walls IAW the latest editions of the National Roofing Contractors Association (NRCA) Roofing and Waterproofing Manual, Sheet Metal and Air Conditioning Contractor’s National Association (SMACNA) and the Architectural Sheet Metal Manual. The Contractor must perform other roofing tasks including but not limited to: installing, repairing, and replacing sheathing, boards, beams, and joists and insulation; opening roofs to install such items as skylights, access doors, vents, ventilators, pipes; fabricating and maintaining gutters and downspouts; coating gutters with aluminum roof coating; and locating roof leaks and making required permanent repairs; clearing roofs of all debris, as required.

        - MATERIALS. All materials used in repair work shall equal or exceed the standard of the existing material. The contractor must comply with the latest NRCA, Roofing and Waterproofing Manual, SMACNA and the Architectural Sheet Metal Manual for materials to be used. All materials must comply with applicable UL and FM standards.

        - EXECUTION. All roof repair /restoration/replacement work shall be performed in accordance with the latest edition of the NRCA Roofing and Waterproofing Manual, the SMACNA, Architectural Sheet Metal Manual and manufacturer’s printed installation instructions for the materials being used.

      - SELF-HELP SERVICES.	The Contractor shall perform the following services when requested on an approved work order form:

        - Order, provide, and issue paint and supplies to government employees for the interior of buildings including brushes, drop cloths, rollers, roller pads, roller pans, masking tape, spackle, sandpaper sheets, caulking and caulking guns. All self-help paint and materials must be provided to the Government within 7 calendar days of Contractor receipt of a self-help request from the Facilities Engineer.

      - MISCELLANEOUS SERVICE WORK. The Contractor shall assist and perform service work covered in this contract in support of other contractors or Government personnel when ordered on an approved work order. This includes, but is not limited to, shutting off utility services, and marking utility lines.

  - CUSTODIAL.

SCOPE. The Contractor shall provide all management, supervision, labor, equipment and materials for custodial requirements as described in this SOW. Custodial service applies to facilities on campus.  Janitorial services for unoccupied facilities may be reduced to quarterly and/or waived at Facilities Engineer direction.

PERSONNEL. Personnel shall present a clean and neat appearance and wear a clean uniform each day.

SUPPLIES. All supplies used, handling and storage of cleaning agents, solvents, cleansers, etc., must follow Federal, State and applicable product instructions. All cleaning equipment and cleaning agents used must comply with applicable standards for safety and noise abatement.

LEVEL 1 - SCHEDULED/PREVENTATIVE MAINTENANCE AND OPERATION.

      - PREVENTIVE MAINTENANCE. The Contractor shall perform custodial services in accordance with daily, weekly, twice weekly, monthly, semiannual, annual, and periodic custodial requirements such as refuse and debris removal, vacuuming, mopping, waxing, buffing, dusting, spot cleaning, or other requirements as necessary. Urinals mats impregnated with urine salt treatment must be placed in ALL urinals on the facility and changed out monthly. The areas must present a clean, professional, uniform appearance and finish always. The Contractor must plan, schedule and perform all custodial services so as not to interfere with official Government business.

      - CUSTODIAL SERVICES PLAN. The Contractor shall provide an Annual Work Plan for custodial services. The initial plan must be prepared and submitted to the Facilities Engineer for review within 60 days. As a minimum, the plan must list the location of each task for each area/room and the scheduled day and time for performing those tasks.

      - PERFORMANCE STANDARDS.	Performance standards for custodial services are as follows:

        - FLOOR CLEANING. The entire floor surface including behind doors, on stairways, landings, stoops, abutments, and on surfaces beneath off-the-floor furniture and equipment must be made free of litter, dust, and debris. Chairs, waste receptacles and other movable items must be tilted or moved to clean underneath. Items moved during floor cleaning must be returned to their original position. Furniture including legs, equipment, wall baseboards, carpets/rugs and floor finish must not be disfigured or damaged by the floor cleaning operations. Floor surfaces must be cleaned flush against walls, doors, furniture including legs, equipment or other stationary objects. Floor surfaces must be cleaned IAW the manufacturer’s recommendations for the material being cleaned.

- CARPET CLEANING. All carpets, area rugs and entry mats must be vacuumed free of all soil, debris and foreign matter. Carpets must be cleaned IAW the manufacturer’s recommendations for the type of fiber and backing. Carpets and rugs must be cleaned free of stains, streaks, and spots so as to have a bright uniform color.

- SHAMPOOING. All carpets must be shampooed at start of period of performance.  Carpets must be shampooed using a machine approved by the Facilities Engineer. Shampooed carpets must be free of all embedded debris, stains, spots, spills, deposits, ink spots, insects and cleaning marks.  Carpets indicated for replacement do not require shampooing.  Facilities Engineer shall provide written direction on exempt spaces.

- SWEEPING/DUST MOPPING. Non-carpeted (e.g., concrete, VCT, LVT, slate, ceramic tile, porcelain tile, etc.) floors, stairways, elevators and landings must be swept and/or mopped so as to remove all debris except embedded dirt and grit. A sweeping compound to reduce airborne dust must be used when sweeping and mopping. A properly swept floor is free of all debris except that which is embedded in the floor. Note: cleaner-treated sweeping mops are referred to as Dust Mops in the frequency schedule in TE-4.

        - MOPPING/SCRUBBING. Mopped or scrubbed floor surfaces must present a uniform, clean appearance free of embedded debris, soiled-water, cleaning solutions, films, streaks, swirl marks, stains, spots and standing water. Mopping or scrubbing solutions must be applied and removed IAW manufacturer’s recommendations. The application of free water, sufficient to stand on the floors or to seep into the flooring joints is prohibited. There must be no splash marks or mop streaks on furniture, wastebaskets, doors, walls or baseboards. Carpeted floors must not be mopped. Wood and LVT floors must be mopped IAW manufacturer’s recommendations. All lavatory, shower, and restroom floors must be damp mopped utilizing an FDA approved germicidal solution.

- DAMP MOPPING. All non-carpeted floors, stairways and landings must be damp mopped using a cleaning detergent or stain removal agent to remove debris or stains remaining on the floor surfaces.

- WET MOPPING OR SCRUBBING. All non-carpeted floors, stairways and landings must be wet mopped and scrubbed to remove soil and debris remaining on the floor surfaces. Floor scrubbing must be accomplished using a deck brush, cylindrical or disc-type machine, or automatic scrubber, utilizing steel wool or synthetic pads using as little water and detergent solution as possible, followed immediately by a clean-water rinse and dry- wrung mop or vacuum pickup.

        - WAXING/BUFFING. The application of wax must be sufficient to provide a continuous, durable, protective coating. Floor surfaces must be waxed IAW the manufacturer’s recommendations for the specific surfaces. All wax used must have nonskid characteristics. Wax must not be allowed to build up along walls or in Facilities Engineers. Buffing of wax before it has completely dried is prohibited. Any wax staining or residue on wall baseboards, thresholds, doors, walls, furniture, and adjacent floors or carpeted areas must be removed. All waxed floors must be buffed IAW manufacturer’s recommended materials specific to the floor. All waxed areas must be buffed for maximum gloss and uniform sheen without leaving buff marks. Baseboards and furniture must not be marred or discolored by the buffing equipment or materials used.

- TOUCH-UP WAXING. Floors must receive one application (coat) of wax and must be buffed to a uniform sheen.

- STRIP AND REWAX. In areas where stripping and rewaxing operations are performed, all wax will be removed from the IAW manufacturer’s recommended instructions. Wax removal is accomplished when surfaces have all wax removed down to the flooring materials. Stripped surfaces must present a uniform, dry, clean appearance free of debris, embedded dirt, dust, deposits, soiled water or cleaning solutions, films, streaks, swirl marks, stains and standing water. The Contractor must seal the floor with an appropriate sealer IAW the manufacturer’s recommendations. Wax applicator must be free of soaps or detergents.

        - DUSTING. Dusted surfaces must be free of dust, dust streaks, lint, cobwebs, dirt, foreign matter and debris. All furniture, radiators, equipment, horizontal ledges, Facilities Engineers and sills must be dusted.

- FURNITURE. Tables, chairs, beds, lockers, bookcases, systems furniture, filing cabinets, counters, carts, desks, and items normally considered furniture must be dusted. Desks or other areas cluttered with Correspondence or other items must not be dusted.

- LOW DUSTING. Dust must be removed from walls, windowsills, door grilles, door frames, shelving, bulletin boards, pictures, frames, fixed wall phones, thermostats, baseboards, wainscoting, pipes, radiators and covers, conduit, equipment, fixtures, furniture, and other items less than six feet from the floor.

- HIGH DUSTING. Dust and cobwebs must be removed from walls, ceilings, and other structural components, air conditioning ductwork, vents, registers, hanging light fixtures, door frames, door closing mechanisms, pipes, equipment, and all fixtures over 6 feet from the floor.

        - LAVATORIES, SHOWERS AND RESTROOMS.  All plumbing fixtures, wall surfaces, partitions, toilet accessories, etc. must be thoroughly cleaned with a neutral soap, non-damaging solution, which includes an FDA approved germicidal agent. This work includes cleaning all exposed, underside and accessible surfaces. The cleaning must be sufficient to remove deposits, stains, debris, streaks, spots, grease, food particles, film, mildew, and must render the space free of odors. Soap dispensers must be filled so that soap is available at all times. Facial quality bar soap must be provided where there is no dispenser. All supply holders, including paper towel, toilet tissue, sanitary napkins and soap dispensers must be appropriately replenished such that there is always sufficient quantity available for use for all patrons. All cleaning must occur at the frequency as recommended in TE-4. The cleaning includes spot cleaning as required, removal of graffiti and polishing to a bright finish. The cleaning of air vents and floor drains is included. Sponges and cloths used in these spaces will not be used in any other types of spaces.

        - MISCELLANEOUS CLEANING. The following items must be cleaned and emptied if appropriate, in accordance with industry standards and manufacturer’s recommendations:

- DRINKING FOUNTAINS

- WASTE RECEPTACLES. The number of trash cans serviced may be adjusted by the Government as much as 5 percent per year without contract cost increases or decreases.

- INTERIOR AND EXTERIOR ENTRANCE MATS. The contractor must provide replacement mats, the same type and size. Any deviation from this should be submitted to the FACILITIES ENGINEER for approval.

- CLEANING ALUMINUM.

- STAIRWELLS AND LANDINGS.

- INTERIOR AND EXTERIOR GLASS AND MIRROR CLEANING.

- WINDOW SCREEN AND FRAMES. Window screens and their metal frames must be cleaned free of dirt and foreign material on both the inside and outside facing surfaces.

- LIGHT FIXTURES. All light fixtures (installed and portable) and their components.

- METAL CLEANING.

- WALLS, CEILING, DOORS AND BASEBOARDS.

- BLINDS.

  - GROUNDS MAINTENANCE.

SCOPE. The Contractor shall provide Grounds Maintenance and landscaping services (including any necessary landscaping design) as described herein or on base.

GENERAL. The Contractor shall be responsible for the management of the total grounds’ maintenance effort. This work includes, but is not limited to, the planning and programming of all services, mowing and trimming operations, fertilization, re-seeding, watering, removing litter, weeding, pruning, planting, and requires compliance with all records and reporting requirements.

DAMAGE TO GOVERNMENT PROPERTY. Damage to roads, grounds, buildings, and other Government property resulting from Contractor’s performance of this contract must be promptly repaired by the Contractor at no cost to the Government.

LEVEL 1 - SCHEDULED/PREVENTATIVE MAINTENANCE AND OPERATION.

      - GROUNDS COVER CUTTING (e.g., lawn areas, grass/weeds/other vegetation). The Contractor shall maintain ground cover areas in a manner that promotes proper health, growth, rich natural green color and neat appearance. Lawn areas are to be free of broadleaf weeds, weedy grasses that present an unsightly appearance, dead vegetation, and debris. All surface disruptions (e.g., rodent and insect mounds), are to be raked level and any resulting holes filled prior to mowing. Grass cutting is to be accomplished in a manner such that it is free of scalping, rutting, bruising, and uneven or rough cutting. Grass clippings must be either mulched or removed immediately after mowing; this determination must be made by the Facilities Engineer. Where practical, each successive mowing must be at approximate right angles to the previous mowing. If any bare ground within the limits of an area included in this contract becomes populated with grass or weeds through natural spread (e.g., not artificially planted) the Contractor must maintain such area(s) as a part of the basic contract. Prior to mowing, the Contractor must remove all refuse, debris, leaves, rocks, paper, and other portable objects within the maintenance area lodged in shrubs, hedges, fences, and along foundation walls. Ground cover is to be maintained at an even height range from 2.5 to 3 inches for tall fescues; ½ to 1 inch for Bermuda grass; and 1-1/2 to 2-1/2 inches for rye grass.

      - EDGING. The Contractor shall perform edging in a manner that is free of scalping, rutting, bruising, and uneven and rough cutting. Vegetation must not be cut back more than 1 inch from pavement. Edging of sidewalks, driveways, curbs, and other paved surfaces, and around gardens and other cultivated areas must be performed in conjunction with mowing.

      - TRIMMING. The Contractor shall trim ground cover around trees, shrubs, cultivated areas, fences, poles, walls, fire hydrants, sprinkler heads, valves, and other similar objects. Trimming must be done in such a way as to avoid damaging the trunk, bark or roots or trees and shrubs. If a bird nest is discovered in the trimming area, the Contractor must ensure that proper coordination or permitting under the Migratory Bird Treaty Act has occurred prior to removing any nests. After trimming, all cuttings and debris resulting from the Contractor’s operations must be collected and disposed of. Trimming within any given parcel must be completed within 1 day of each mowing.

      - PLANT AND SHRUB PRUNING. The Contractor shall prune all shrubs, bushes, hedges, and other cultivated plants facilities Engineering to their natural growth habit, for proper health, attractive appearance and to prevent interference with pedestrian and vehicle traffic. Pruning is to be done in a manner that: prevents growth in front of windows, over entrance ways and walks; prevents obstructing vision at street intersections; removes dead, damaged, or diseased wood, and naturally forms and balances the shrubs, bush, or plant. Ornamental must be pruned to accommodate their flowering cycle, pruning of the entire plant or shrub must be performed not less than once per year to maintain their established shape and appearance. Prune to maintain the plants natural form except for formal hedges. Always prune back to an outward facing bud. All pruning must be performed facilities Engineering to applicable Alabama Cooperative Extension standards.

      - TREE PRUNING. The Contractor shall prune all trees facilities Engineering to their natural growth habits, to evenly form and balance the tree, to promote proper health and growth, and to prevent interference with pedestrian and vehicular traffic. Pruning is to be done in a manner that removes dead, damaged or diseased wood, or structurally weak limbs that may cause a safety hazard; removes branches that extend over buildings, endanger roofs, eaves and windows; cuts back branches that are within 5 feet of building walls or overhang or grow into power lines or lamps; anticipates the effects of wind on branches which might fall on power lines; shapes the entire tree rather than notch the top; and prevents growth of small trees in front of windows and over entrance ways or walks which will obstruct vision at street intersections. If a bird nest is discovered in the trimming area, the Contractor must ensure that proper coordination or permitting under the Migratory Bird Treaty Act has occurred prior to removing any nests. Prune facilities Engineering to National Arborist Association for pruning and maintaining shade trees.

      - WEED CONTROL.  The Contractor shall perform weed control to prevent the encroachment of weeds into established landscapes, including lawn areas and around trees, shrubs, flower beds, etc. Plant beds and special landscaped areas must receive weed control to eliminate unsightly and/or noxious weeds. Weed control in all plant beds must be performed by pulling the weeds by hand or using Facilities Engineer approved chemicals. The Contractor must submit data concerning proposed chemical use prior to utilization. Additionally, weed control must be performed to eliminate grass and weeds in cracks and joints within or along sidewalks, curbs, and roads within or adjacent to the maintenance area. All areas to be treated and chemicals to be used must be prepared, applied and disposed of in strict compliance with the product’s labeling and with all Local, State, and Federal (EPA) requirements. The chemicals to be used and the rate and method of application must be specified in the Contractor’s Annual Grounds Maintenance Plan.

      - DEBRIS REMOVAL AND DISPOSAL.  The Contractor shall remove all debris and pick up these areas a minimum of twice each week to remove unsightly or inordinate accumulation of foreign material, leaves, bark, limbs, dead vegetation, paper, refuse, pallets, etc. All cuttings (grass, etc.) and debris resulting from the Contractor operations must be removed from the work site prior to the end of the workday. Debris removal and pick up must be performed for the entire maintenance area, including trash accumulated in waste receptacles, walkways, stairways, curbs, fences, shrub and flower beds, window wells, interior courtyards, and quadrangles, terraces, and exterior air intake grates/grills. Dead vegetation, any material that will support combustion, and trash must be removed from limited growth areas prior to accumulation or when required due to a recent storm. Debris removal must be performed to prevent unsightly or inordinate accumulation including trash accumulated in waste receptacles.

Existing downed trees and storm damage removal shall be addressed within 120-days of start.  An allowance is available for performance of this task.  Debris removal work in excess of this dollar value shall first receive prior written approval from the Contracting Officer, Facilities Engineer, and Program Manager.

        - DISPOSAL OF REFUSE. Paper and other refuse collected as part of grounds maintenance must be disposed of off Government property IAW Federal, State, Local and TRACEN Birmingham Regulations at the Contractor’s expense.

      - IRRIGATION. If on the 1st day and 15th day of the month from April through October it has not rained an average of 1” per week, the Contractor must irrigate to assure at least an average of 1” of water per week including rain in order to provide the necessary soil moisture to obtain proper growth and color. Average rainfall must be determined by the Contractor on a weekly basis.

        - The Contractor’s irrigation work includes periodic watering of lawns, shrubs, trees, ground cover plants, and flower beds in the specified areas. Care must be exercised by regulating the time and equipment to prevent wasting water. Watering of turf must be accomplished only during the early morning between 0400-0630. Watering must be done in a manner that will avoid erosion and runoff or ponding due to excessive quantities or rate of application.

        - The Contractor shall perform routine maintenance and repair of installed systems including sprinkler systems but not limited to: a) maintaining valve access covers and sleeves in good repair and free of debris; b) exercising valves; c) winterizing all systems including draining and addition of antifreeze if needed; and d) repair of underground piping, valves, and fittings damaged by freezing, Contractor’s neglect, or Contractor’s equipment. Permanently installed sprinkler heads must be kept clear for approximately 1-inch around their outside circumference by a chemical herbicide treatment or trimming. Dirt or other debris surrounding sprinkler heads, which impair or prevents proper operation of the sprinkler heads, shall be removed.

        - Any depressions or mounds around the base of newly planted trees and shrubs, intended to retain irrigation water in place, shall be maintained in good condition by the Contractor to permit the most efficient application of water and reduce waste. The Contractor shall be responsible for any damage to plants, lawns or buildings caused by careless handling of sprinkler equipment. Sprinklers must not be set in such a position as to throw water into doorways, windows, porches, parked cars, tennis courts, parking areas, or to impede vehicular and/or pedestrian traffic.

        - The Contractor shall remove hoses, portable sprinklers, portable pipe, and similar irrigation equipment from lawn areas at the end of each workday or when not actually in use. All valves, covers, and valve box covers must be kept always closed except when in actual use. The Contractor shall coordinate irrigation with the FACILITIES ENGINEER so as not to interfere with Command activities.

        - The Contractor shall abide by any Local, State, or other water agency’s regulation or controls in force at the time of this contract and the Government reserves the right to reduce or eliminate watering work during water shortages and drought. The Contractor will not be held responsible for replacement of dead plants or lawns caused by the elimination or reduced watering imposed by the Government.

      - SURFACE DRAINAGE. Whenever necessary, the Contractor shall remove obstructions (i.e., vegetation, debris, leaves, soil) to water flow in ditches, gutters, catch basins, storm drains curb inlets, filter’s and gratings. Soil depressions resulting from accumulation of excavation or rutting caused by vehicles, tractors, and other mobile equipment must be filled with topsoil, graded to conform with the surrounding area, and vegetation replaced. Catch basins must be inspected quarterly, and cleaned as necessary to prevent sand, stone, or other heavy debris from entering underground drainage systems.

      - FLOWER BED PLANTING AND MAINTENANCE. Flower bed planting will not be required in year 1.  All flower beds should receive a fresh coating of mulch within 90-days of start and 8 months after.

      - SHRUB BED MAINTENANCE AND TREE MULCH. Contractor shall quarterly inspect all tree and shrub beds for evidence of disease, pest infestation, or any other harmful condition and edge back turf to establish original shrub bed border. All mulch must be replaced on an annual basis. The mulch pile must have a recessed top to catch water rather than repel it.

      - WINTER DAMAGE REPAIR. The Contractor shall repair all damaged areas of turf in all Ground Maintenance Levels in March; fill and level holes, cracks, or eroded areas with topsoil; re-sod any damaged area bigger than one half square foot, otherwise reseed; and keep seed/sod moist until mature and healthy.

      - LEAF REMOVAL. This includes leaves, pine needles, fir needles, and other fallen vegetation so as to prevent an unsanitary, unsightly, or unkempt appearance. The Contractor shall collect the removed leaves and other vegetative debris.

DOCUMENTATION AND RECORDS

      - ANNUAL GROUNDS MAINTENANCE PLAN.  The Contractor shall prepare an Annual Grounds Maintenance Plan.  At a minimum, the Annual Work Plan must list the location of each task and the proposed frequency for accomplishing each task. The Plan must be tailored to the requirements of local conditions, types of vegetation and climatic factors.

      - SURFACED AREA SWEEPING. The Contractor shall sweep all sidewalks, roadways, and other paved areas, excluding areas designated for vehicle parking, once every month with equipment normally used for this type of operation.

      - PAVEMENT MARKING. Pavement markings which become obliterated must be restored IAW the Alabama Department of Transportation specifications for roads.  Pavement marking repainting must be done in the same color as specified in applicable standards and must be coincident with old markings resulting in straight, clear cut clean lines. Immediately after a line has been repainted, the Contractor must place traffic cones to prevent vehicular traffic from driving on the wet paint and “tracking” the fresh paint onto the road surfaces. Placement of these traffic cones must be accomplished for all pavement paint work performed under this contract. Traffic cones must be picked up by the Contractor as soon as the paint has dried. All work under this contract must be accomplished in such a manner as to minimize the disruption of traffic flow. At no time must an entire intersection be blocked by freshly applied paint.

      - EARTH SURFACE ROADS, PATHS, AND TRAILS. The

Contractor shall maintain and repair earth surface roads, paths, and trails.

This work includes the following:

        - Maintain shoulders to allow proper surface drainage to prevent ponding, and to protect the road edge. Grass or other treatment may be required to prevent erosion.

        - Maintain gravel and other earth surface roads by blading or dragging the surface until all ruts and holes are filled. Maintain a smooth surface and a uniform crown that encourages drainage away from the crown and prevents ponding on the surface.

        - Haul fill material to earth surface roads, paths, and trails as necessary to use for filling in ruts and holes.

      - SIDEWALKS AND CURBS. Sidewalks and curbs must be maintained as specified in the following:

        - CRACKS AND FAILURES. All deteriorated and broken sidewalk and curb areas must be removed to the original joint sections and must be replaced with materials similar to the original construction. This includes portions displaced due to settlement and upheaval caused by tree roots, etc.

        - DISPOSAL OF EXCAVATED MATERIAL.  When

ordered by the Facilities Engineer, the Contractor shall remove designated excavated material to an appropriate off-site disposal area. Excavated material may include materials excavated by the Contractor, another authorized Contractor, or Government personnel. Only if authorized in advance by the Facilities Engineer may excavation material be spread elsewhere on Government property; otherwise, the Contractor is responsible for off-site disposal IAW State and Local ordinances.

  - REFUSE COLLECTION AND DISPOSAL.

SCOPE. The Contractor shall schedule and perform all refuse collection and disposal services. Work includes collection and disposal from the following types of containers: 6, 8 and 40 cubic yard capacity dumpsters, 90-gallon residential garbage with covers (located at the housing units), various exterior garbage receptacles and cigarette butt receptacles. Work also includes collection and disposal of large items such as Christmas trees, empty crates, packing materials, equipment and vehicle parts as well as recycling.

GENERAL. The Contractor shall collect, remove, and dispose of all refuse. The Contractor must provide all dumpsters. The Government will provide residential garbage receptacles, residential recycling receptacles, exterior garbage receptacles, and cigarette butt receptacles. All areas which are involved in the collection and disposal services must be maintained in a neat, clean, uniform, and safe condition at all times. All refuse collection and disposal tasks described herein are the Contractor’s responsibility under the firm-fixed-price portion of the contract.

HOURS OF OPERATION. All refuse collection services shall be performed between the hours of 7:30 a.m. and 5:00 p.m., Monday through Friday as well as during these same hours on weekends when prescribed, excluding federal holidays. Deviation from the contractor’s approved Refuse Collection and Disposal Plan must require prior written approval by the Facilities Engineer. The Contractor must not be responsible for any refuse collection on federal holidays. The Refuse Collection and Disposal Plan must address how the Contractor plans to reschedule and accomplish pickups affected by the holidays. Refuse collection must be scheduled so as to not interfere with government functions and special events. The Contractor will be given advance notice of these events.

      - POINTS OF COLLECTION (POC). The Government reserves the right to direct the Contractor to relocate any or all refuse pickup stations, and the Contractor must adjust their service to meet relocations without additional cost to the Government.

        - CONTAINER HANDLING. The Contractor shall return non-disposable containers to their proper station in an upright position with the lids securely in place.

        - FALLING/WIND BLOWN DEBRIS. The Contractor shall maintain all collection points in a neat, clean, uniform and sanitary condition. All refuse falling during removal operations must be picked up and removed by the Contractor. All refuse within 20 feet of collecting points must be picked up and removed.

        - INCENDIARIES/EXPLOSIVES/HAZARDOUS WASTE OR MATERIALS.  If incendiary or other explosives, hazardous waste or other hazardous materials are found at a collection site, or at any location on campus, the Contractor shall not disturb or pick up the material. The Contractor shall immediately call the Facilities Engineer.

        - ITEMS OF VALUE. The Contractor shall not dispose of any material which has obvious value and appears to have been inadvertently placed near the collection point without Facilities Engineer approval.

      - GARBAGE CONTAINER MAINTENANCE. All garbage containers shall be kept clean and odor free and maintained in a serviceable condition. Provide plastic liners for all exterior garbage receptacles.

        - SANITATION REQUIREMENTS. The Contractor shall ensure that all garbage containers are steam cleaned and sanitized inside and out at least once.  Contractors shall leave the area clean and free of debris at the end of the day. Washing must be performed in a manner that precludes contamination or pollution of the surrounding area. Notify the Facilities Engineer at least 2 hours prior to cleaning any containers. Scheduling of this requirement must be reflected in the contractor’s approved Refuse Collection and Disposal Plan.

      - RECYCLING. U.S. Coast Guard intends to implement a targeted recycling program at this site.  The contractor shall develop a Recycling Plan and participate in the government’s recycling program by recycling materials generated and encountered to the maximum extent practical. As a minimum, a recycling collection container must be placed by each copier and must be emptied on an as needed basis. Recycling containers must also be placed in areas where materials requiring recycling are likely to be accumulated. Outdoor recycling containers must be designed to prevent water from rain events and pests from getting into containers.

Containers must be clearly marked for recycling and must be in plain view. Each co- mingle recycling container must be clearly marked with highly visible and legible “Co- mingled Materials for Recycling Only”, and a list of all acceptable materials that can be placed in the Co-mingle container. A recycling symbol must also be present on the container. These markings must be professionally printed stickers, signs, or an integral part of container’s manufactured design.

      - REFUSE DISPOSAL. All refuse shall be transported and disposed of by the Contractor in a State of Alabama-approved container to a State of Alabama-approved landfill or refuse collection site. All permits and licenses pertaining to refuse collection, transportation and dumping must be the responsibility of the Contractor. The Contractor shall not store refuse in vehicles or dump it in unauthorized areas.

      - TRUCK STANDARDS. All refuse collection vehicles used by the Contractor shall be specifically designed for the purpose and be compatible with the bulk containers utilized and approved by the Alabama Department of Transportation for the use intended. Bodies of packer-type trucks utilized by the Contractor must be leak proof and fully enclosed. All equipment utilized to collect refuse must be maintained in an operationally safe, serviceable, clean and sanitary condition at all times.

      - REFUSE COLLECTION AND DISPOSAL PLAN. The Contractor shall prepare a Refuse Collection and Disposal Plan to cover all work to be performed under this Section. This plan must be submitted to the Facilities Engineer for review and approval with the Contractor’s Annual Work Plan.

  - CAMPUS SECURITY

Campus security shall be provided 24 hours per day, 7 days a week, 365 days per year.

During the prescribed work day, 7:30 am to 4:30 pm a total of 3 security personnel must be on duty at all times.  One security person shall man the security building at all times.  One security person shall perform roving security functions while a third remains “on call” for any emergent issues.  Two security vehicles are required on site during the work day.  One to be used for roving security.  One to be used for emergent responses.

After hours, 5 pm to 8 am, a total of 2 security personnel must be on duty at all times.  One security person shall man the security building at all times.  The second security person shall perform roving security and respond to any emergent issues.  One security vehicle is required on site overnight for the performance of roving security.

Federal holidays and weekends require 2 security personnel on duty at all times with roles and responsibilities aligning with after hours staffing.

Security vehicles must be marked and readily identifiable as such.

A total of 16 FTE personnel are anticipated to satisfy these requirements.  All security personnel must have a valid background check and have at minimum 2 prior years experience in security or law enforcement fields.  One individual shall be designated as the security forces manager.  This individual shall create duty schedules and handle all administrative functions for security personnel.  The security forces manager must have a minimum of 6 years experience in security or law enforcement with at least 2 years experience in a managerial role for security personnel.  Security personnel must be included in the organization chart to be submitted for Coast Guard review and approval.

Security personnel must stop all vehicles entering campus and ensure valid identification.  Once established as a Training Center, no individuals without a common access card (CAC) or on an approved access log shall be permitted to access campus at any time.  Guests may be added to the approved access log but should be cleared at least 24 hours prior and require escort by a CAC approved individual.

Roving security guards must make continuous rounds of all paved roads and manned facilities.  The roving security guard and security building guard may alternate duties within an assigned shift.

All security personnel on duty shall be readily available via radio.  The Facilities Engineer and Commanding Officer shall be provided radios for convenient communication with security personnel on duty.

A Campus Security Plan must be developed within 15-days of start and submitted to the Contracting Officer and Program Manager for review and approval.  Subsequent updates shall be submitted to the Facilities Engineer for review and approval.  The Campus Security Plan shall be updated upon transition to an official Coast Guard Training Center to ensure alignment with established Coast Guard policies.

  - PEST CONTROL.

- SCOPE. The Contractor shall schedule and provide all pest control services in all grounds, facilities and equipment to include:

- Household Pest Control

  - Structural Pest Control.

  - Control of Pests of Medical Importance.

- Miscellaneous Pest Control.

- GENERAL. The Contractor must perform the following tasks each time pest control services are performed:

  - Inspect the site completely.

  - Identify pests, pest damage, or any potential for pest infestation.

  - Determine the extent of the pest problem.

  - Utilize non-chemical controls (e.g., traps) or pesticide application methods authorized by the label and as approved by the Facilities Engineer to obtain the control required.

  - Remove any nuisance wildlife using the least harmful method. Attempts must be made to turn over injured animals to the local SPCA or other wildlife agencies.

  - Evaluate the effectiveness of the treatment.

  - Maintain records of all actions taken. These records must be available for inspection by the Government upon request and turned over to the Government at the completion of the contract.

- PESTICIDES. All pesticides used by the Contractor shall be registered with EPA for the use intended. All pesticides require approval of the Facilities Engineer prior to use. All pesticide usage must be in strict conformance with label directions. The Contractor must maintain a label book for all pesticides used and have it readily available for reference and Government inspection.

- EQUIPMENT. The Contractor shall maintain, use, calibrate and store equipment and attachments per the manufacturer’s recommendations and instructions, IAW with Federal, State and Local requirements to pose no harm to humans or the environment.

- VEHICLES. Vehicles used to transport pesticides must be equipped with a fire extinguisher, spill and decontamination kit, emergency wash water, and eyewash.

  - APPEARANCE. All vehicles shall be maintained free from observable pesticide spills or residue.

- NOTIFICATION OF PEST PROBLEMS. The Contractor shall report to the Facilities Engineer, any evidence of pests or conditions conducive to pest infestation within 1 working day of the time such condition is first discovered.

- PESTICIDE SAFETY. No space treatments must be made in occupied spaces until all occupants and pets have vacated the premises as required or recommended by the pesticide manufacturer. The Contractor shall coordinate with building occupants 1 week in advance so they can make arrangements to vacate the area or premises before any application of pesticides.

- CONTAMINATION. Particular care must be taken to ensure that food, water, or other substances subject to ingestion by humans or pets are not contaminated by pesticides. The Contractor must provide clean, uncontaminated plastic tarpaulins to protect dishes and other household items that could be contaminated by pesticide applications. If utensils, work surfaces or machines used to prepare or dispense foods are inadvertently contaminated, the Contractor must immediately clean the contaminated item, or, if appropriate, dispose of the item when approved by the FACILITIES ENGINEER. The Contractor must warn occupants of the necessity for cleaning food-contact surfaces after any pesticide application and specifically inform them of any inadvertently contaminated areas.

- PESTICIDE APPLICATION. The Contractor shall apply pesticides in such a manner as to prevent toxic exposure of personnel, pets, wildlife, ornamental plants, beehives, and any other non-target components of the environment. The Contractor shall not apply pesticides during heavy rain while runoff is occurring. The Contractor must have a current copy of each label for each pesticide being used. SDS for all chemicals used on the TRACEN must always be available for inspection by the government.

- RUNOFF. The Contractor shall ensure that toxins do not run off as surface flow, or contaminate any ditch, culvert, drainage system or standing or flowing body of water.

- PESTICIDE SECURITY. All pesticides and their dispensers must be secured in a locked storage facility or vehicle or must always be under the immediate and direct control of the Contractor while on Government property. All pesticide dispensing

equipment, including bait stations and trays, must be clearly and plainly marked “DANGER – CONTAMINATED WITH PESTICIDES” and must include the name and concentration of the pesticide. The use of bait stations and trays must be IAW Federal, State and Local requirements.

- RODENTICIDES. Rodenticides must be placed in covered bait stations except when placed in traps or located in places inaccessible to pets or humans. (Inaccessible means that effort must be exerted to move equipment, etc., to expose the bait or its container.)

- PESTICIDE BAITS. Pesticide bait must not be broadcast applied unless prior approval is obtained in writing from the FACILITIES ENGINEER. Prior to broadcasting, the area involved must be secured from entry by humans or pets.

- PESTICIDE WASTE. All pesticide waste, rinseate, and residue must be stored in IAW Federal, State and Local requirements. It must be stored until such time as sufficient quantity, as determined by the Defense Property Disposal Office (DPDO), is accumulated for transfer to DPDO. The Contractor must turn over waste and residue to DPDO as directed by the Facilities Engineer.

  - EMPTY CONTAINERS. Empty pesticide containers must be disposed of by the Contractor IAW Federal, State and Local laws and regulations. The Contractor must triple-rinse containers with clean water each time, IAW current requirements of EPA and the RCRA.

- SPRAY EQUIPMENT USE. The Contractor shall use spray equipment in strict accordance with manufacturer’s instructions. The Contractor must warn occupants of adjacent buildings prior to spraying. As directed by the Facilities Engineer, the Contractor must repair or replace, at no cost to the government, property and non- target vegetation damaged as a result of careless or inappropriate application of any material being applied by spray.

- RESIDUAL PESTICIDE APPLICATION. Pesticide applications in food preparation and storage areas, and around food dispensing machines and water fountains, must be limited to crack and crevice treatment. The underside of all tables and equipment, including drawer runners and tubular legs, must be treated in a similar manner. The contact individuals for the facility or quarter’s occupant are responsible for preparing the area to be treated. Such preparations include moving all furniture away from walls prior to the arrival of the Contractor. The Contractor is not responsible for removing shelf paper, food, and other items from cabinets and closets prior to treatment. If the area has not been properly prepared, the Contractor must not perform the service as scheduled, and must immediately report the circumstances to the Facilities Engineer.

- INDOOR ULTRA-LOW DOSAGE (ULD) APPLICATIONS.	The Contractor shall properly secure the space to be treated when ULD applications are used. The Contractor must post a sign on each outside door warning against entry without proper protection. The Contractor must notify Security, Safety Officer and medical clinic at least 1 day in advance of ULD applications.

- ENDANGERED SPECIES. All pest control activities must be accomplished in a manner that ensures maximum protection of endangered species and environmental quality IAW PL 91-190, National Environmental Policy Act; PL 93-205, Endangered Species Act of 1973; Executive Order (EO) 11643, Environmental Safeguards, 8 Feb 72; and EO 12088, Federal Compliance with Pollution Control Standards, 13 Oct 78.

- MAJOR PESTICIDE SPILL AND CLEAN-UP. The Contractor shall contain and report immediately to the Facilities Engineer any major pesticide spills. The Contractor shall then decontaminate and clean up the contaminated area. Decontamination must be accomplished by the IAW label and other published directives pertaining to specific pesticides. A major pesticide spill is defined as one that involves the spillage or leakage of 1 quart or more of concentrated or diluted pesticide onto or into any floor, roof, culvert, gutter, drain, catch basin, paved or unpaved surface, land area, commodity, or standing or flowing body of water of any size whatsoever.

      - WOOD INFESTATION INSPECTION. The Contractor shall annually inspect all structures to determine any infestations or visible damage to wood structural components.

        - QUALITY STANDARDS. The contractor shall prepare and submit an accurate and complete written report with graph or description of location, nature, and extent of infestation and visible damage, submitted within 10 working days of inspection.

      - RODENTS. The Contractor shall establish a rodent control program to eradicate rodents. The Contractor must place poisoned bait only in distinctively marked, spill-proof bait stations. Bait stations must be maintained around building perimeters,

sewage lift stations, in sewer manholes, and any other areas as required to eliminate rodent activity. Detailed location records of bait stations must be maintained by the Contractor. Anticoagulant tracking powder, pelletized package, or paraffinized baits must be used to treat crawl spaces and utility runs as required.

        - QUALITY STANDARDS. The Contractor’s efforts shall be sufficient to prevent rodent damage to stored products; no sightings and no physical evidence of rodent activity; and, using the black light/ultraviolet method of surveillance, no evidence of rodent urine spots on commodities.

      - MOSQUITO SPRAYING. The Contractor will have the base sprayed for mosquitoes during the months of June – September.

      - LARVAL MOSQUITOES. The Contractor must treat standing water for mosquito larvae.

        - QUALITY STANDARDS. All areas treated as scheduled.

      - CARCASS DISPOSAL. The Contractor shall remove and dispose of all dead or dying rodents or other animals, and birds treated under an eradication program.

        - QUALITY STANDARDS. Carcass removal and odor neutralized in accordance with an approved work order from the Facilities Engineer.

      - TICKS, FLEAS AND CHIGGERS. The Contractor shall respond to requests to control ticks and chiggers with residual insecticides.

        - QUALITY STANDARDS. Outside of buildings: Using a tick drag or dry ice surveillance techniques, no activity for 72 hours after treatment. Inside of buildings: No visible signs of activity for 7 days after treatment.

      - SPRAYING. For Grounds Maintenance Levels B and C, spraying and removal of hazardous pests such as bees, wasps, etc., will be completed when ordered on a work order.

      - HOUSEHOLD PEST CONTROL. The Contractor shall provide control of occasional or accidental invading or nuisance pests.

        - QUALITY STANDARDS. No visible signs of activity for 30 days after treatment.

      - VENOMOUS ARTHROPODS. The Contractor shall control venomous arthropods with residual insecticides in and around buildings, transportable garbage containers, recreational areas such as picnic grounds, and other areas. Honeybee swarms must not be destroyed if a practical alternate method is available for their removal. Pests to be controlled include bees, wasps, spiders, and such others as may be designated by the Government.

        - QUALITY STANDARDS.	No visible activity for 24 hours after treatment.

      - FLIES. The Contractor shall treat for biting and non-biting flies in and around refuse containers.

      - MISCELLANEOUS PEST CONTROL

      - STRUCTURAL PEST CONTROL. Subterranean Termite Control: The Contractor shall provide control of subterranean termite’s facilities Engineering to the provisions of the National Pest Control Association’s Approved Reference Procedures.

        - QUALITY STANDARDS. The treatment shall last 5 years against re-infestation or damage.

    - DOCUMENTATION AND RECORDS.   The Contractor shall maintain, complete, and submit records and reports specified herein.

      - TREATMENT LOG. The Contractor shall maintain a complete chronological record of all pest control operations. The record must contain date, location, task performed, pesticide and concentration used, method of treatment, and name of target pest. Accurate and complete records of pest control operations must be recorded by close of business on the day on which the services are completed.  Treatment logs shall be submitted to the Facilities Engineer monthly.

      - PEST MANAGEMENT PLAN. The Contractor shall prepare an annual Pest Management Plan. The Pest Management Plan must be prepared and submitted to the Facilities Engineer. Only those prescriptive pesticide applications as shown in the approved Pest Management Plan must be performed by the Contractor during the contract period, unless otherwise directed by the Facilities Engineer. Changes to the Pest Management Plan must be requested in writing by the Contractor and submitted to and approved by the Facilities Engineer prior to implementation. To facilitate Facilities Engineer review of each pesticide specified in the Pest Management Plan, the Contractor must submit copies of either the EPA or State of Alabama registered pesticide labels (as directed by the Facilities Engineer). The following minimum information must be included for each pesticide specified in the Pest Management Plan:

- Area to be treated (e.g., Maintenance Level and Parcel Number).

- Pests treated for (e.g., snakes, roaches, flies, rodents, etc.).

- Approximate time and frequency of application.

- Common name and EPA or State of Alabama registration number of each pesticide product.

- Rate of application (e.g., ounces/100 LF).

- Form of pesticide as received from supplier, and form in which pesticide will be applied (e.g., wet-table powder, dry crystal, etc.).

- Any special precautions, not on labels, which are necessary/required to prevent environmental damage or personal injury.

- A verifiable listing of the Contractor’s State of Alabama categories of pesticide applicator licensing, name of license holder in each category, and State of Alabama license number.

- Method of disposal of old or unused hazardous material (e.g., pesticides, herbicides, etc.) and empty containers which contain hazardous materials.

# DELIVERABLES.

The Contractor shall submit the following deliverables as required by other sections of the SOW; either in hard copy, on electronic media (CD) or through email. All documents should be compatible with Microsoft Office.

| Deliverables | Frequency | No. of Copies and to Whom | Submitted Proposal/Date Required |
| --- | --- | --- | --- |
| Annual Work Plan | Within 90-days start | Two/One Facilities Engineer/Contracting Officer |  |
| Safety Plan | Within 90-days start | Two/One Facilities Engineer/Contracting Officer |  |
| Monthly Work Schedule | Monthly | One/Facilities Engineer | 15th of month due |
| Monthly Report of Contractor’s Activity | Monthly | One/Facilities Engineer | 7th of month |
| Initial and Annual Equipment Inventories | Within 90-days start; within 90-days end | One/Facilities Engineer |  |
| Work Summary (Backlog) Report | Weekly | One/Facilities Engineer | IAW SOW |
| Work Order Project File | For each active Work order | Facilities Engineer access upon request | As agreed, |
| Certificate of Insurance as Required by FAR 52.228-5 | Annually | One/ Facilities Engineer | 10 days after award |
| Organization Structure/Staffing Plan | Within 90-days start | Two/ Facilities Engineer & Contracting Officer | When updated |
| Resume: Engineering Management, Civil Engineer, Master Electrician | Within 90-days start | Two/ Facilities Engineer & Contracting Officer | When updated |
| Volatile Organic Compound (VOC) Compliance Plan | Annually | Two/One Facilities Engineer/Contracting Officer | 10 days after award |

# PERSONNEL REQUIREMENTS/QUALIFICATIONS

  - ADMINISTRATION AND MANAGEMENT. The Contractor’s work and responsibility shall include all planning, programming, administration, and management necessary to provide all services as specified. The Contractor must perform all related Contractor administration services necessary to perform the work, such as but not limited to supply and warehousing, quality control, job order shop operation, financial control, and maintenance of accurate and complete records, files, and libraries of documents to include Federal, State and Local regulations, codes, laws, technical manuals, and manufacturer’s instructions and recommendations, which are necessary and related to the functions being performed. The Contractor must provide related services such as preparing and providing required reports, compiling historical data, performing administrative work, and submitting necessary information as specified. Tasks must be performed in such a manner as to conform to the standards specified in this contract.

  - PERSONNEL. The Contractor shall submit an Organization Structure and Staffing Plan to the Facilities Engineer within 90-days of start as well as when a management change occurs. At a minimum, the following information must be included: the names of the Project Manager (Engineering Management), Civil Engineer, Master Electrician and contact information for on-call designated individuals. In addition, the number of personnel assigned to each specific trade must be indicated.

    - PROJECT MANAGER/ENGINEERING MANAGEMENT. The Contractor shall designate a Project Manager who must: (a) be thoroughly familiar with the requirements of this contract, and (b) possess the necessary qualifications and abilities to manage the execution of this contract. The resume of the nominated individual must be provided to the Facilities Engineer, Contracting Officer, and Program Manager. Upon approval by the Facilities Engineer, the Project Manager must be designated in writing to conduct overall management coordination and must be the central point of contact with the Government for performance of all work under this contract. Should a new Project Manager be assigned while the contract is in force, the Contractor must comply with these provisions for designation and notification except that the submission of a resume letter must be within 24 hours of selection of the individual for replacement as Project Manager. The Contractor must ensure that the duties of the Project Manager will be always executed by a qualified, designated individual approved by the Facilities Engineer.

      - DUTIES AND AUTHORITY. The Project Manager or their designated alternate shall be physically present on-site during normal working hours. The Project Manager or their designated alternate must be available within 30 minutes during normal working hours and within 2 hours during all other times (24 hours per day, Monday through Sunday). For emergency response, at any time, the Project Manager, or their designated alternate(s) must be at the scene of the emergency within 2 hours. The cellular telephone numbers of the Project Manager and their alternate(s) must be provided to the Facilities Engineer and Program Manager within 15 days of contract start date and any time there is a change in these numbers or personnel. The Project Manager and their designated alternate(s) must have full authority to act on the behalf of the Contractor for prompt action on matters pertaining to Contractor performance of this contract. The Project Manager and any alternate must have authority to negotiate individual task orders for up to $100,000. The Contractor must provide notification to the Facilities Engineer and Contracting Officer in advance each time the designated Project Manager will be absent for more than 24 hours and an alternate Project Manager is performing the duties of the Project Manager.

      - QUALIFICATIONS. The Project Manager is a full-time position. The individual must have a minimum of 8 years’ experience as a project manager or engineering manager of a multi- disciplined workforce performing facilities maintenance functions. The Project Manager must demonstrate proficiency in both written and oral communication and in the preparation of detailed cost proposals.

        - In addition to the above project management experience, the Project Manager must have either:

- Any combination of 5 additional years of experience as: a journeyman craftsman in the construction or facility engineering field; design or construction management experience in the engineering field; or construction/facility related experience in the business field or

- A 4-year Engineering degree from an accredited college.

      - ALTERNATE PROJECT MANAGER. The Alternate Project Manager is a full-time position. The Contractor shall assign one or more designated alternates to the Project Manager to act in their/her behalf during absences such as illness, vacation, etc. A written resume and notice of such designation must be provided to the Facilities Engineer for approval. The qualifications of any Alternate Project Manager must be the same as the Project Manager except they must have a minimum of 5 years of experience as a Project Manager or Alternate Project Manager of a multi-discipline work force performing facilities maintenance functions. In order to supply a diverse mix of skills, experience and training, the project manager and the assistant project manager should have different specialties.

        - DUTIES AND AUTHORITY. The designated Alternate Project Manager shall perform all the duties and have the full authority of the Project Manager stated in Section 8.2.1.1 in the absence of the Project Manager.

  - OTHER PERSONNEL. The Contractor shall provide qualified personnel to accomplish all contract work and services within specified time frames.

  - CONTRACT EMPLOYEES. Personnel in a training status must not be substituted for qualified personnel. Personnel having an experience level below journeyman must at all times be under the immediate supervision of a person with an experience level at or above journeyman as appropriate to the occasion.

    - PROOF OF CITIZENSHIP OR LEGAL RESIDENCY.  All Contractor employees must be citizens of the United States or, if aliens, they must be legal residents of the United States. If aliens are hired, proof of legal residency in the U.S. must be provided to the Facilities Engineer prior to their commencing work under this contract.

    - CERTIFICATION AND LICENSES. The Contractor shall provide personnel who possess the appropriate certificate or license as required in the locality or, as an alternative, with the skills and qualifications specified in the latest edition of the DOL Service Contract Act Directory of Occupations unless otherwise indicated in 29 CFR 4, Paragraphs 4.152 and 4.6(b)(2) where specific certification or license is not required.

    - HAZARDOUS MATERIAL/WASTE COORDINATOR.  The contractor’s Hazardous Material/Waste Coordinator shall be trained and knowledgeable in Hazardous Waste Regulations.

    - FIRE SYSTEMS TECHNICIAN. The contractor shall provide a certified fire alarm and fire sprinkler technician I.A.W., the Nation Fire Protection Association and NICET Level II certified.

    - HEATING, VENTILATION AND AIR CONDITIONING TECHNICIAN.  The contractor shall provide at least two HVAC technicians with a minimum of 5 years’ experience maintaining similar type and size commercial equipment. The contractor must provide only certified, knowledgeable technicians experienced in servicing the equipment.

    - ELECTRICIAN. at least one full-time person possessing a license as a Master Electrician with High Voltage experience is anticipated to be required. NEC states that all work over 600 volts is considered High Voltage.

    - EVIDENCE OF CERTIFICATION, TRAINING AND LICENSES.  The Contractor shall provide the Facilities Engineer with evidence (e.g.., certificate of training, license) that all required certification, qualification, and training has been received by each employee working in each functional area having these requirements. This must be accomplished 15 days prior to contract start date, for proposed employees, and within 5 days of when a new Contractor employee is hired to perform work in those functional areas.

  - ABILITY TO COMMUNICATE. Contractor personnel shall be able to speak and comprehend the English language with the degree of fluency sufficient to perform their duties to meet contract requirements. Contractor personnel must be able to read and comprehend materials

in English. This must include materials such as instructions, regulations, manuals, training materials, and other written materials that personnel will be required to use in the performance of their duties. The contractor employees must be capable of writing in English to adequately meet contract requirements. Examples of the type of written materials required in Contractor personnel performance of duties are the Technical Exhibits attached to this Performance Work Statement, regulations and instructions identified in Paragraph 4, and the manufacturer’s manuals for equipment.

  - CONTRACTOR EMPLOYEE IDENTIFICATION.

Contract employees must be eligible to obtain a CAC card. This card requires a National Agency Check (NAC) and successful completion of an FBI fingerprint check. Failure to accurately complete the eQIP package may result in revocation of the CAC credentials.

The contractor must ensure that employees who resign or are terminated surrender both their CAC card and keys. The contractor must ensure that the Command Security Officer and the base security contractor are immediately notified by telephone of the employee’s departure.

Each employee must be easily recognized as a contractor employee. Contractor personnel requiring entry into Government facilities (e.g., secure areas, housing units) must present their identification card upon request.

  - SECURITY REQUIREMENTS. The Contractor shall comply with all facility security requirements, security regulations and directives as identified herein, and other security requirements cited elsewhere in the contract. The Contractor must submit for approval to the Facilities Engineer a Contractor-initiated state police basic security check for each member of the proposed work force to ensure integrity, honesty, and trustworthiness within 90-days of start. For any subsequent hiring, the basic security check must be submitted to the Facilities Engineer prior to the employee start date at no cost to the government.

    - SECURITY CLEARANCES. No special security clearances are required to perform the work under this contract. However, upon request, the Contractor shall submit the name and address of each employee hired to work on this contract and must direct the Contractor employees to fill out questionnaires and other forms as may be required by the Facilities Engineer for security.

    - ACCESS TO GOVERNMENT COMPUTER WORKSTATIONS.  Contract Employees that require any access to USCG workstations in order to perform their duties must complete all required access paperwork required by the IT department.

  - KEY CONTROL. The Contractor shall establish and implement methods of preventing the loss or misplacement of keys or use by unauthorized persons. Unauthorized utilization of keys by Contractor employees may result in the banishment of the individual from the Training Center. A listing of Contractor employees authorized to utilize keys will be submitted to the Facilities Engineer within 90 days of contract start. Keys must not be duplicated.

    - LOST KEYS. The Contractor shall report the occurrence of a lost key immediately to the Facilities Engineer. In no event must the report be later than the next day. The Contractor must be required to replace, re-key or reimburse the Coast Guard for replacement of locks or re-keying as a result of Contractor losing keys. In the event a master key is lost or duplicated without authorization, all locks and keys for that system must be replaced by the Contractor at no cost to the Government.

    - IMPROPER USE OF KEYS. It is the responsibility of the Contractor to prohibit the use of keys to Government facilities, vehicles, or equipment by any persons other than the Contractor’s authorized employees or authorized Government personnel. The Contractor must not open locked areas to permit the entrance of unauthorized persons therein.

    - INVENTORY OF KEYS. The Contractor shall provide an inventory of the keys to the Facilities Engineer within 45-days of start. This inventory must include an actual physical count of all keys. Key inventory shall be repeated every 6 months.

# GOVERNMENT QUALITY ASSURANCE

  - REWORK/REPERFORMANCE. The Contractor shall perform or re-perform any work which was not originally performed in a satisfactory manner, at its own expense.

    - RESPONSIBILITY AND ACCOUNTABILITY. The Contractor shall assume responsibility and accountability for all workspaces and take adequate precautions to prevent fire hazards, odors, chemical spills, vermin, and infestation. Contractor-occupied facilities are subject to fire and safety inspection by the Government. Any fire or safety hazards produced by Contractor action or inaction must be corrected by the Contractor, at no cost to the Government, within 48 hours of written notification. The Contractor must keep the work areas neat and clean, and in good condition and repair.

  - EQUIPMENT. Existing equipment will be furnished in an “as is” condition. The Contractor shall be responsible for all service, maintenance, and repair, to include parts and labor, for the equipment. This requirement also pertains to all applicable preventative maintenance. Service and maintenance of all Government provided equipment must be listed in the Contractor’s annual work plan. The Contractor must not cannibalize any Government equipment during the contract period.

    - EQUIPMENT INVENTORY. The Contractor and the Facilities Engineer must jointly determine and record condition of all equipment. The Government may replace or repair items not in working order; however, the Facilities Engineer may direct the Contractor to replace the missing items or accomplish repairs for which the Contractor will be reimbursed. The Contractor and Facilities Engineer must certify in writing their agreement on inventory and working order of equipment.

    - ACCOUNTABILITY AND RESPONSIBILITY. The Contractor shall maintain a current equipment inventory. Not later than 20 days prior to the completion or termination of the contract, an inventory of equipment must be conducted and certified in writing by the Contractor. This will be verified by the Facilities Engineer. The Contractor must be liable for loss or damage to equipment beyond reasonable wear and tear IAW the clause entitled, “Government Property”. All equipment in need of repairs/maintenance must be repaired by the Contractor before the inventory is made. In the case of items lost or damaged beyond economical repair, the amount of the Contractor’s liability must be the depreciated replacement value of the item; this value will be determined by the Facilities Engineer.

      - GOVERNMENT USE OF EQUIPMENT. Upon 24 hours written or oral notice to the Contractor, the Government is authorized to use any government- provided vehicles or equipment under the Contractor’s control. In an emergency, the Government may require immediate use of equipment without prior notice. The Contractor will not be held liable for any damage incurred by the Government to equipment.

    - EXPENDABLE PARTS, SUPPLIES AND TOOLS.	The Government will provide funding for an initial supply of expendable parts, supplies and tools.  Prior to purchasing any parts, supplies, or tools an inventory  of existing materials must be provided to the Program Manager within 10 days of start. Following inventory completion, contractor shall identify by written report to the Contracting Officer and Program Manager initial supplies, parts, and tools required for contract performance.  This report must include numbers and quantities to be purchased, tasks targeted for completion with these materials, and an itemized cost estimate. Upon receipt, these items must be jointly inventoried by the Contractor and the Facilities Engineer within 2-days. The Contractor must give the Facilities Engineer at least 1-day advance notice of the date to commence this inventory, method of accomplishment and the number of people involved. The value and content must be documented by this joint inventory with Facilities Engineer signature and joint submission to the Contracting Officer and Program Manager.

    - TURN-IN PROCEDURES FOR EXPENDABLE PARTS, SUPPLIES AND TOOLS.  At the completion or termination of the contract, the Contractor must return to the Government a supply of expendable parts, supplies, and tools not consumed. The Contractor and the Facilities Engineer or their representative must jointly conduct an inventory of parts, supplies and tools not later than 15 days prior to the end of the contract. The Contractor must give the Facilities Engineer at least 30 days’ notice of the date of this inventory, method of accomplishment and the number of people involved.

  - SUPPLIERS’ CATALOGS. The Contractor shall keep an up-to-date library of suppliers’ catalogs. Catalogs must be updated as new issues are published by suppliers.

  - UTILITIES. The Government will fund heat, air conditioning, water, electricity, sewer, and other utility services.

  - COMMUNICATION FREQUENCIES. The Government will provide/assign communication frequencies that may be utilized by the Contractor.

  - MAINTENANCE CART OPERATION.   Contractor-operated maintenance carts must not be driven or parked on single-width (four feet wide or less) sidewalks or in any manner that blocks any sidewalk. Contractor-operated maintenance carts must not drive on grass or other unpaved areas at any time.