Statement of Work

BOILER REPAIR & WELDING SERVICES

CENTRAL UTILITY PLANT & NIST CAMPUS

AT THE

NATIONAL INSTITUTES OF STANDARDS AND TECHNOLOGY

GAITHERSBURG, MD

Date:  December 16, 2025

Statement of Work (SOW) STATEMENT TABLE OF CONTENTS

- Background Information

- Purpose

- Place of Performance

- Regular business Hours

- Period of Performance

- Specific Requirements / Tasks

TASK 1: 	General Conditions

TASK 2:		ASME Welder & “R” Stamp Requirements

TASK 3: 	Steam Manholes

TASK 4: 	Welder Qualification

TASK 5:		Work - General Requirements

TASK 6: 	Callback Response

TASK 7:		Concept of Operations

TASK 8:		Authority for Work

- Special Conditions

- Safety

TASK 1: Safety Related Requirements

Task 2:  Safety Related Training

- Homeland Security Presidential Directive (HSPD)-12

- General Requirements

11.  Badging

12.  Issuance Of Building Keys

13.  Government Furnished Material

14.  Inspection & Acceptance

15. Payment Schedule

- BACKGROUND INFORMATION

The National Institute of Standards and Technology (NIST) is a government scientific research facility located in Gaithersburg, MD. The facility buildings largely date to the early 1960’s.

NIST operates a Central Utility Plant (CUP) to deliver several site-wide utility services to the campus buildings. Primary amongst that service is the production of high-pressure steam. This steam production consists of 6 standard boilers and a high efficiency COGEN system. Loss of the capability to provide steam to the NIST Campus jeopardizes the national mission NIST is tasked with.

Generally, most boiler repairs, piping, and associated repairs within the NIST CUP involve American Society of Mechanical Engineers (ASME) certified welding, and a R-Stamp from the American society of Mechanical Engineers (ASME) The “R” stamp is required for boiler shell and internal repair.

This contract operates off a fixed dedicated allocation. The contractor is only paid for authorized services, as needed and approved by the government.

- PURPOSE

NIST is seeking an ASME “R” stamp qualified boiler repair and welding contractor to perform high pressure steam piping and boiler repair and mobile welding operations on a 24/7/365 callback basis for urgent CUP repairs and limited other repairs in site steam manholes and other spaces on a as needed basis.

- PLACE OF PERFORMANCE

Work is primarily located at building 302, NIST, Gaithersburg, Maryland.

- REGULAR BUSINESS HOURS

Regular business hours are Monday through Friday, 6 AM to 6 PM Eastern Time, excluding Federal holidays and NIST closures.

- PERIOD OF PERFORMANCE

The period of performance for this project is for the base year, and up to four option years.

6.   SPECIFIC REQUIREMENTS

TASK 1: 	General Conditions

- Contractor to provide all labor, transportation, materials, facilities, equipment, and personnel necessary to provide on-call critical maintenance/repair for six high pressure power boilers and the CoGen and/or their support systems and other associated systems.

- Generally, the boilers are:

  - SG-1 44,000 PPH Union Iron Works Boiler S/N 22951

  - SG-2 44,000 PPH Union Iron Works Boiler S/N 22952

  - SG-3 44,000 PPH Union Iron Works Boiler S/N 22957

  - SG-4 44,000 PPH Union Iron Works Boiler S/N 22958

  - SG-5 80,000 PPH English Boiler Model APP80250 S/N 960391

  - SG-6 80,000 PPH English Boiler Model APP80250 S/N 960392

  - HRSG 80,000 PPH RENTEC Boiler S/N 2015-39 (C-Gen)

- The contractor will, on an as needed basis conduct repairs within the Gaithersburg NIST CUP on steam and power generating boilers and associated piping and components per applicable ASME and code requirements.

- Boiler repairs include but are not limited to welding repairs on water wall tubes, economizer tubes, generating tubes, pier tubes, front header, sidewall headers, rear header, mud drums, steam drums, power piping, blow down drains, valves, safeties, hand holes, manholes, baffles, and gas passes.

  - Boiler repair shall also include the boiler envelope and associated support systems.

  - The support systems include the boiler, boiler tubes, boiler steam piping, feed water systems, piping, and related components and assemblies. This will include the rolling of tubes into the headers and the replacement of tubes.

  - Contractor will have all equipment and personnel to respond to emergency response calls within 8 hours of notification.

  - Contractor is solely responsible for supplying all labor and materials for repairs.

  - Contractor will demolish and reinstall insulation on piping, boilers, pressure vessels, and valves removed to affect repairs or investigation.

TASK 2:	ASME Welder & “R” Stamp Requirements

1. Generally:

- The contractor will have minimum ten (10) years current experience repairing high pressure boilers working within the ASME “R” code.

- Contractor will have and maintain ASME welding certification and NBBI “R” certification at time of bid submission and during the life of the contract.

- Loss of the “R” certification shall be cause for immediate termination of the contract.

- Contractor will also have staff certified to the ASME welding code applicable to requirements of the “R” stamp for other general piping repairs.

      - No other welder certification will be acceptable for any work on this contract.

      - Contractor will provide certificate of ASME certification at time of bid submission and during the life of the contract.

      - Loss of ASME welding certification shall be cause for immediate termination of the contract.

TASK 3:	Steam Manholes

- Contractor will perform work in steam manholes at temperatures up to 180 degrees Fahrenheit, usually less, when incorporating multiple blowers continuously or other cooling equipment.

- Contractor shall independently verify interior manhole piping conditions.

- Contractor will have personnel trained in confined space entry per OSHA regulation.

- Contractor will supply and utilize all confined space equipment required for code compliant entry and work in confined spaces.

- Contractor will be solely responsible for all OSHA confined space entry documentation, record keeping, training, and equipment required for confined space entry.

TASK 4:		Welder Qualification

- All work and individual welder qualifications shall be to American Society of Mechanical Engineers (ASME) Section IX.

    - The contractor and welding staff will be qualified to make welds complying with “R” code requirements.

    - The contractor will have all tools, welding machines, tube rollers, and material available to complete all repairs.

    - Contractor shall provide individual welder certifications to COR or designee as part of submittal process before any work commences.

          - Welding staff qualifications will be updated as welding staff is added or changes.

    - Contractor shall provide welding procedure to COR for approval for butt weld and socket fitting welds no later than 10 days after notice to proceed, and prior to any welds being made.

    - No X-ray or other NDT requirement unless required by NBBI code requirements or specifically requested by COR.

    - Following any services performed the contractor will furnish a written report detailing what repairs were made along with copies of employee certifications, NBBI and ASME boiler inspection reports for repairs and if employee certifications were required for the repairs.

TASK 5: 		Steam and Condensate Steam Piping General Requirements

- The following general conditions shall be utilized at a minimum for the installation on steam system piping in and in manholes.  Deviations from these conditions shall be approved by the COR.

  - All pipe utilized, including threaded nipples, shall be of nominal size schedule 80 seamless pipe.

    - All weld fittings on condensate piping and condensate system components will be rated ANSI 150# or equivalent.

      - Where condensate return piping is replaced including flanges for valve installation, match original weights. Where new piping is installed to replace failed condensate piping 300# class flanges and valves shall be the replacement.

      - Valves in steam and condensate return will be OSY cast steel valves: Crane or equal.

    - All weld fittings on steam piping and steam system components will be rated ANSI 300# or equivalent.

  - All welds shall be made “uphill” and any weld found to exhibit or found to be made downhill (starting from top of pipe to the bottom) shall be totally removed and remade.

  - Contractor shall provide sketches of piping to be replaced prior to starting fabrication

TASK 6: 	Callback Response

- The contractor will have a 24 / 7/ 365 on-call system and have direct or authorized facilities located within the NIST Gaithersburg local commuting area.

- There shall be a telephone number for 24-hour service requests. Calls for service will go to a live representative and will not be automated.

- Service provider shall maintain an on-call notification system of mandatory escalation to management to ensure notification is made.

- Initial response (telephone) to a call for service shall not exceed 2 hours.

- Contractor will have all equipment and personnel to respond to emergency response calls within 8 hours of notification.

# TASK 7: 	Concept of Operations

- Described as follows is the established process the Government will utilize for call outs and repairs as well as stated standards for deliverables.

  - Central Plant personnel identify an emergency repair or maintenance that needs to be addressed.

  - Contracting Officer’s Representative (COR) or Contracting Officer (CO) make initial contact with contractor utilizing an established and approved contact procedure with request to evaluate the repair that has been identified.

  - The contractor must arrive on site within the required 8-hour period to evaluate the identified deficiency.

  - The Government is responsible for coordinating site and building access to the installation during a call out.

  - The contractor will respond with only fully Green Badged – Out of hours Access personnel for all responses.

  - The contractor will coordinate with NIST CUP Shift Supervisor then analyze the deficiencies and to the maximum extent possible inform the COR of progress being made.

  - Progress should be documented and submitted in writing (email) daily.

  - Within one (1) day after inspection of any component for which the contractor recommends repairs or replacement, submit a proposal in-person or via email on company letterhead to the COR.

    - Where system component parts are required, specifically state availability, provide a cut-sheet, and a lead-time if part(s) require procurement.

    - If defects in components are discovered, which, in the contractor’s opinion, are optional to correct, the contractor shall submit a letter describing the defect.

    - The CO will review the information provided by the contractor and decide whether or not to make the optional repair.

  - Each proposal shall include a detailed listing of all components, to include descriptive nomenclature, and likely manufacturer as well.

  - Each proposal shall also include a description of the recommended repair or replacement, cost proposal and estimated time to complete the recommended work (after Notice-to Proceed has been received).

  - Each proposal shall show itemized material and subcontractor costs, as well as labor hours and rates.

  - The CO will review each proposal submitted. If the recommended repair is approved the Contractor will be issued a Notice-to-Proceed for the repair.

  - For approved repairs, furnish all needed parts and repair services, welding, machining, and reshaping components to restore within code requirements, industry norms, and or manufacturer’s specified tolerances.

  - The COR / CO may add inspection items to the proposal based on the type of work included in the accepted proposal.

  - The contractor will provide a final cost report to the COR within 10 days of completed repair

  - The contractor will submit a “paper copy” of invoice to COR before submission to NIST Invoicing.

# TASK 8: 	Authority for Work

- On notification by COR or designee, contractor will respond with a crew to the NIST CUP to access the repair requirements within 8 hours.

- Within 24 hours, the contractor will provide the COR a written estimate for repairs with sketches, material list, and estimated labor.

- The work authorization may only be granted by the Contracting Officer or authorized designee.

- An itemized list of the materials, parts, and labor hours needed to complete the repairs will be submitted to the Contracting Officer at the conclusion of work being completed by the contractor.

The government will reimburse the contractor for the initial response and estimate creation, approved labor, and parts and materials approved by COR to return the high-pressure power boiler, or its subsystems, to operational condition.

7.  Special Conditions

1.	Contractor is solely responsible for providing required safety equipment.

2.	 Contractor shall provide arc shielding as required to shield arc welding visibility by passing vehicular or pedestrian traffic.

3.	The drawings obtained from NIST may or may not be up to date, therefore, may not reflect the as-build condition. Contractor shall not consider these documents as as-built without field verifications.

4.	Asbestos or asbestos containing material may be found in this area.

a.	If any suspected asbestos is encountered, contractor is to stop work immediately and contact COR. NIST will expedite the asbestos removal to the best of its ability.

8. SAFETY

NIST is committed to maintaining a work environment that safeguards the public and the environment, as well as personnel and property.

1.  Within 5 days of contract award, the contractor shall provide COR with an OSHA compliant safety plan for contract activity.

a.  The Safety Plan shall specify how the company’s policies and practices will comply with each of the applicable standards, laws, and codes.

2.   The contracting officer will approve or provide written comments regarding the plan to the contractor within seven (10) days of receipt.

a.  Contractor will submit a revised safety plan within seven (7) days with required information for the contracting officer to review.

b. This cycle may be repeated, if necessary, until the contracting officer determines the safety plan to be acceptable.

TASK 1: 		SAFETY RELATED EQUIPMENT

The Contractor shall:

  - Provide all safety-related equipment required to perform the work under this award, including personal protective equipment (PPE) and other equipment that is required or appropriate to protect contractor personnel and other personnel on the NIST campus.

  - Contractor-provided personal protective equipment shall include, at a minimum, hard hats, safety shoes, safety glasses (prescription or standard), respiratory protection (powered air purifying respirator or full-face mask respirator), high visibility clothing and gloves that meet applicable OSHA standards for PPE.

TASK 2: 		SAFETY RELATED TRAINING

The Contractor shall:

- Provide safety-related training required by applicable OSHA, state and local regulations or standards to affected contractor personnel (including subcontractor personnel) that perform work under this award.

    - Such training may include, for example, training for proper use of PPE, respirator use, fall protection, crane operation, forklift operation; electrical safety, or other safety-related topics.

- Maintain records of safety training provided to contractor personnel (including subcontractor personnel) that perform work on this award.

- The contractor shall make those records available to the contracting officer, contracting officer’s representative for the award, or other authorized personnel within 3 business days of receipt of their written request, and annually thereafter or upon request.

9.  Homeland Security Presidential Directive (HSPD)-12

1. The Contractor (and/or any subcontractor) and its employees who require physical access to NIST facilities or logical access to NIST IT networks or systems must comply with Homeland Security Presidential Directive (HSPD)-12, Policy for a Common Identification Standard for Federal Employees and Contractors; OMB M-05-24; OMB M-19-17; FIPS 201, Personal Identity Verification (PIV) of Federal Employees and Contractors; NIST HSPD-12 policy; and Executive Order 13467, Part 1 §1.2.

- THIS SECTION APPLIES TO THIS CONTRACT WITH REGARD TO BADGING – SEE BADGING SECTION BELOW

- Position Sensitivity Designations Requirement

- The following position sensitivity designation levels apply to this solicitation/contact:

Low / None

10.  GENERAL REQUIREMENTS

- A notice to proceed / kick-off meeting cannot be held until the safety plan is approved.

- Within 10 days of Notice to Proceed provide submittals for contract materials.

- Within 7 days of notice to proceed, provide a schedule for contracted work.

- Contractor shall provide COR a weekly update (**) on all project activity via email with the following information due on the Tuesday after the week being reported on:

- Adherence to projected schedule (on time or other)

- Daily employee list and hours

- Major work activity

- Task completion percentages

- Problems encountered

- Changes to scope or methodology

- Change orders (Pending, presented, and completion on project (%)

- Other items that affect timely completion of contracted work or project conditions.

- Due Thursday by 2Pm during the term of contract.

(**) During periods of inactivity the contractor shall submit an abbreviated report.

- The Contractor(s) shall be on the NIST grounds only between the hours of 6:00 a.m. and 5:30 p.m. (normal work hours) on normal Federal work-days.

  - Should the Contractor(s) desire to work at times other than those specified above, the dates and hours must be scheduled in advance and approved by the NIST Security Office through the Contracting Officer.

  - After hours work will require a government approved escort 100% of the time.

- Contractor personnel are required to wear identification badges at all times on the NIST grounds.

- The Gate “F” at the National Institute of Standards and Technology site shall be used for material supply and personnel by the Contractor and subcontractors unless otherwise directed by the COR or during out of hours access.

- See “GUIDELINES FOR OFPM CONTRACTORS AND A/E FIRMS PERFORMING SITE INVESTIGATIONS AND FIELDWORK (including construction) AT THE NATIONAL INSTITUTE OF STANDARDS AND TECHNOLOGY GAITHERSBURG, MD”.

- BADGING

# The Contractor(s) shall be on the NIST grounds only between the hours of 6:30 a.m. and 6:00 p.m. (normal work hours) on normal Federal workdays.

# Green Badge applications for responding staff and supervisors will be submitted for afterhours access due to the nature of this contract for all response personnel.

# After hours work will require a government escort 100% of the time.

# Non- U.S. citizens to be employed under this contract must have official legal status in the U.S.

# The federal government requires Real ID or a valid passport for identification purposes.

# Real ID requirements apply for badge applicants and anyone requiring entry onto the NIST Campus. This includes delivery personal or other administrative staff or support personnel.

# Contractor personnel are required to wear identification badges at all times on the NIST grounds.

# The gate “F” at the National Institute of Standards and Technology site shall be used for material supply and personnel by the Contractor and subcontractors unless otherwise directed by the COR or during out of hours access.

# Afterhours access (after 4:30PM during the work week) will be via the main gate.

# Any vehicle with a company logo, cargo bins, or with equipment / trailers must be inspected at Gate F during duty hours, and or by security staff at the front gate during out of hours entry.

# The contractor agrees that they are the primary authority in getting their personnel and sub-contractor’s badges for site access.

# The contractor will within 15 days of Notice to Proceed provide to the COR a complete list of personnel and sub-contractor personnel requiring badging.

# Contractor will provide legal names as shown on official identification (driver’s license, state ID)

# Contractor will identify any non-resident aliens to begin the additional verification requirements for access.

# Contractor will provide all contractor and sub-contractor personnel position descriptions for all names submitted.

# Contractor is advised to include delivery drivers and other supervisory staff for contractor and any sub-contractors.

# Contractor will be responsible for ensuring all personnel being submitted for badging have a daily monitored, and active email address for everyone.

# Contractor will be provided an electronic “-	OFPM NIST Associate Badge Application and OF-306 Form” that each submitted employee is required to fill out. Other forms will be required to be submitted as determined by the NIST Badging Office.

# Contractor will return all completed forms to the COR within 10 workdays.

# Contractor is responsible for ensuring all fields are complete and information is correct.

# Forms can only be returned electronically by password protecting the forms individually.

# Contractor and COR will coordinate on password to be used.

# Password changes will be communicated immediately.

# Contractor is advised the fingerprinting process has recently changed at NIST.

# Effective January 1, 2023, all fingerprinting actions, to include those fingerprints captured for hiring actions (EQIP) and those captured for Badging, will be completed using the US Access credentialing system located in the Badge office at NIST Gaithersburg or other US Access Share Service locations.  To facilitate this, all Federal Employees, Associates, and Contractors who require a PIV, PIV-I or Facility Access Credential will need to be enrolled in the US Access system by requesting an appointment for an enrollment within the US Access scheduler.

# Here is the direct link to the US Access Scheduler.

# Contractor is required to have at least one person credentialed to be an approved escort.

# Requires a 1 hour online course once Green Badged

# Requires a visit to the Badge Office for escort badge issue.

# More than one person can take this training at contractor’s prerogative.

# Paper Visitors Passes are limited to a 14-visit limit and should not be used unless no other option is available.

# 14 pass limit includes authorizations to visit submitted but not utilized.

# 14 pass limit is not for the calendar year, but a year from first issuance.

# Out of hours work:

# Contractor shall utilize NIST Outage Paper Badging

# Contractor shall provide name, citizenship status, and other required information to COR to be added to the access list within 14 days of planned installation onsite.

# Urgent / expedited work will be expedited to the extent possible.

# Non-resident aliens require additional paperwork for access. Allow at least 10 days for processing.

12.  ISSUANCE OF BUILDING KEYS

Does not apply to this contract.

13.  GOVERNMENT FURNISHED MATERIAL

- The Government is not providing any property, material, or equipment for this project.

14.  INSPECTION & ACCEPTANCE

- The contractor shall complete all work tasks in a workmanship manner, complete and leave a fully functional system.

- The COR or appointee (CUP personnel) will inspect all work for completeness, functionality, adherence to approved proposal, and operational requirements.

15. PAYMENT SCHEDULE

- Contractor will invoice only once per month.

  - Contractor will submit a “paper copy” of the invoice for review and approval by COR prior to submitting to the government for payment.

  - Certified payroll will be submitted to COR prior to submitting invoice to the government for payment.

  - Final payment, is allowed in the same month a previous payment has been made, providing all closure documents (release of claims, completed punch lists, final certified payroll, and other required documentation) has been submitted and approved.