## Sheet3
Salient Characteristics
| Palce of Performance: WBAMC Loading Dock |  | Date:5/7/2026
| Requirement POC: |  | Quantity: 1
| Description: Water treatment Trailer |  | RP#:
Summary: Mobile Sterilization trailers will need a seperate means of treating their supply water do to the special requirements needed for the cold water, hot water, and RO for final rinse.
# | Description of Minimum Requirement and/or Objective | Minimum Requirement | Objective
1 | 60 gpm RO unit | 1 | 60 gpm RO unit. Permeate should be able to drain to nearby trench drain. Use
1a | RO membranes | 8 | Replacement RO Filters
2 | 2000 Gal Water storage tank | 1 | 2000 gal Water storage tank
3 | Chemical Injection Quill | 1 | Chemical Injection Quill
4 | Multibag Filter Housing | 1 | Housing to use 40 inch filters for prefiltering water of sediment and particles.
4a | Bag filters | 100 | .1 Micron Absolute rating
4b | Filters | 100 | .5 micron Absolute 40-inch filters
5 | 7.5 HP Water Pump | 1 | 7.5 HP vertical distribution pump
6 | VFD | 1 | 10 HP 460 V
7 | Bladder tank | 1 | 44 Gallon stainless steel vessel w/ bladder
8 | Globe valve | 1 | 1" for blending water to meet Water quality requirement of sterilization equipment.
9 | TDS meter | 1 | GF Signet 9950 to measure TDS in mg/l
10 | Water softner system | 1 | Water softner to soften water going to RO and water Heaters.
11 | Electric Heaters | 4 | 120 v electric heaters
12 | 120 Gal Electric Water Heaters | 2 | Hot water supply. Must be able to keep the hot water between 120-140 degrees Faranheit.
13 | 2 gpm Recirculating pump | 1 | For recirculating hot water
14 | Containment | N/A | Equipment should fit inside of a 52' tractor trailer with a wood flooring so holes can be made for routing pipe.
15 | Maintenance | N/A | Maintenance plan should be provided to maintain the individual equipment and the structure. Maintence plan to include on-call personel.
16 | Installation | N/A | Must include turnkey installation of equipment. Must include connection of equiopment to each other and to the mobile sterilization unit(s).
17 | Site Visit | N/A | Must include site visit to see availability of exsisting utilites and availble space.
18 | Monthly water testing | N/A | Monthly water test to test cold water and hot water supply.
18a | Min Sediment Filtration | MIN-MAX | Cold Water: 0-5 Micron Hot Water: 0-5 Micron
18b | Total Hardness as CaCo3 | MIN-MAX | Cold Water: 50-170 ppm CaCo3 Hot Water: 0-17 ppm CaCo3
18c | Total Dissovled Solids | MIN-MAX | Cold Water: 100-170 ppm Hot Water: 50-250 ppm
18d | Total Alkalinity as CaCo3 | MIN-MAX | Cold Water: 70-180 ppm Hot Water: 50-180 ppm
18e | pH | MIN-MAX | Cold Water: 6.5-8.5 Hot Water: 6.5-9.5
18f | Conductivity | MIN-MAX | Cold Water: 0-1000 umhos/cm Hot Water: 40-500 umhos/cm
18g | Total Silica | MIN-MAX | Cold Water: 0-50 ppm Hot Water: 0.1-2.5ppm
18h | Chloride | MIN-MAX | Cold Water: 0-10 ppm Hot Water: 0-10 ppm
18i | Cu-Copper | MIN-MAX | Cold Water: 0-0.1 ppm Hot Water: 0-0.1 ppm
18j | Fe-Iron | MIN-MAX | Cold Water: 0-0.1 ppm Hot Water: 0-0.1 ppm
18k | Zn-Zinc | MIN-MAX | Cold Water: 0-0.1 ppm Hot Water: 0-0.1 ppm
18l | Al-Aluminium | MIN-MAX | Cold Water: 0-0.1 ppm Hot Water: 0-0.1 ppm
18m | Mn-Manganese | MIN-MAX | Cold Water: 0-0.1 ppm Hot Water: 0-0.1 ppm
18n | Color/Clarity | N/A | Water must be colorless

## Sheet2
|  | Cold Utility |  | Hot Utility
Specification | Units | min | max | min | max
Min Sediment Filtration | Micron | 0 | 5 | 0 | 5
Total Hardness as CaCo3 | ppm CaCo3 | 50 | 170 | 0 | 17
Total Dissovled Solids | ppm | 100 | 500 | 50 | 250
Total Alkalinity as CaCo3 | ppm | 70 | 180 | 50 | 180
pH |  | 6.5 | 8.5 | 6.5 | 9.5
Conductivity | umhos/cm | 0 | 1000 | 40 | 500
Total Silica | ppm | 0 | 50 | 0.1 | 2.5
Chloride | ppm | 0 | 10 | 0 | 10
Cu-Copper | ppm | 0 | 0.1 | 0 | 0.1
Fe-Iron | ppm | 0 | 0.1 | 0 | 0.1
Zn-Zinc | ppm | 0 | 0.1 | 0 | 0.1
Al-Aluminium | ppm | 0 | 0.1 | 0 | 0.1
Mn-Manganese | ppm | 0 | 0.1 | 0 | 0.1
Color/Clarity | Water should be colorless