STATEMENT OF WORK

B2 1330 Fume Hood Replacement

U.S. Department of Commerce

National Institute of Standards and Technology

Boulder, Colorado

02/10/2026

I. BACKGROUND INFORMATION

The Department of Commerce campus is located at 325 Broadway in Boulder, Colorado and is a research & development facility. It consists of the agencies of NIST, NOAA and NTIA. The Office of Facilities and Property Management, OFPM, of the National Institute of Standards and Technology (NIST) is responsible for the maintaining and renovation of spaces consisting of laboratories, office space and facilities maintenance areas, except the David Skaggs Research Center. The requirements as presented in this document, along with any attachments, are intended to describe the minimum Government requirements.

It is the intent of this Scope of Work to provide the requirements for the NIST B2 1330 Fume Hood Replacement Project. This project is to remove and replace the existing fume hood and rooftop mounted exhaust fan in building 2 room 1330.

See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

II.  PURPOSE

This project is for the Applied Chemicals and Materials Division. Building 2 Lab 1330 has an existing tabletop fume hood and associated rooftop exhaust fan installed in 1992 that has reached the end of its intended service. New research will be taking place in the lab that will utilize larger equipment that utilize toxic gases. The existing hood is not large enough the new research equipment being performed within the lab.

This project will be removing and replacing existing counter tops, plumbing, sinks, and reworking existing electrical wiremold, conduits junction boxes, and electrical wiring to accommodate the removal and replacement of the existing fume hood, ductwork and rooftop mounted exhaust fan.

The Contractor shall coordinate with the Government Contracting Officer’s Representative (COR) all activities required throughout the duration of this task order. The Contractor shall communicate with the COR and the CO on all matters pertaining to the task order.

PLACE OF PERFORMANCE

NIST Boulder Campus

Building 2 Lab 1330

325 Broadway

Boulder, CO 80305

Regular Business Hours

See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

PERIOD OF PERFORMANCE

The B2 Fume Hood Replacement shall take 6 months to complete from the date of award.

III. SPECIFIC REQUIREMENTS/TASKS

PART 1: WORKING AT NIST

- Comply with the attached project specifications and the “General Instructions for Conducting Work at the NIST Boulder Campus” requirements.

- The contractor shall refer to existing facility construction drawings and project requirements.

- The contractor shall verify the accuracy and correctness of all existing building information provided.

- The contractor shall coordinate with the Government Contracting Officer’s Representative (COR) all activities required throughout the duration of this contract. The contractor shall communicate with the COR and the Contracting Officer (CO) on all matters pertaining to the contract.

# PART 2: TASKS

Meetings related to the tasks below will include:

- Virtual project kickoff meeting prior to NTP

- Weekly in-person OAC meetings throughout project duration.

Task 1 – CLIN 001 (Base Scope) shall include, but is not limited to, the following work:

- Demolition

  - Architectural

    - Remove adjacent countertop, sink and cabinet base. Sink has a non-friable asbestos coating on the bottom and shall be disposed of per regulations.

    - Remove, shorten and reinstall uni-strut used to hold gas canisters to make room for new fume hood.

    - Remove portions of existing vinyl wall base to accommodate new fume hood and countertop.

    - Provide dust and debris protection for existing equipment located in Lab 1330.

  - Mechanical

    - Remove existing fume hood and associated base cabinet.

    - Remove existing exhaust piping from fume hood to rooftop mounted exhaust fan as directed.

    - Remove exhaust fan, exhaust duct, associated supports, and controls to exhaust fan on adjacent roof.

  - Plumbing

    - Disconnect existing sink and countertop mounted eyewash and rework existing plumbing for new sink and eyewash connections.

  - Electrical

    - Remove existing electrical equipment connections connected to existing fume hood and existing exhaust fan. Any circuits not being reused should be removed back to source.

    - Remove existing wiremold and undercabinet light above countertop. Wiremold to be shortened and reinstalled above new countertop.

    - Disconnect existing lightning protection system from exhaust fan duct

    - Remove existing explosion proof receptacle and conduit back to closest electrical box.

    - Demo existing “cut and exposed” conduit and conductors next to existing light switches. conductors should be removed back to source

  - Fire Alarm

    - Remove existing fire alarm system connection/panic button conduit, junction boxes and conductors from fume hood and exhaust fan to nearest junction box.

- New Work:

  - Architectural

    - Provide and install countertop, sink and base per plan.

    - Caulk, patch and paint interior concrete/concrete block walls.

    - Provide and install new vinyl wall base.

    - Patch, repair and refinish concrete flooring in area of work.

    - Design, provide and install fume hood exhaust stack supports.

    - Provide new exhaust fan roof curb flashing and seal.

    - Provide structural design documents for exhaust fan stack support.

    - Provide and Install exhaust fan stack supports per structural design documents.

    - Patch, repair and reseal existing plexiglass window that the exhaust duct passes through.  Contractor shall field verify the condition of existing plexiglass window. Provide and install new plexiglass window if reuse of existing plexiglass window is not feasible.

  - Mechanical

    - Provide and install new walk-in fume hood per plan and manufacturer’s specifications. Rework sections of existing duct to connect fume hood to new exhaust fan outside.

    - Provide and install new rooftop mounted hazardous exhaust fan, duct connections, exhaust stack and roof work per plan.

  - Plumbing

    - Reconnect existing plumbing pipes and make connections to new sink and countertop eyewash station.

  - Electrical

    - Provide and install new electrical circuits to connect to exhaust fan and fume hood.

    - Provide and install 10’ of cable tray and cable tray waterfalls from existing cable tray to fume hood pass thru to route user instrument cables. Cable tray to be bonded to electrical system.

    - Shorten and reinstall existing wiremold above countertop and adjacent to new fume hood as needed.

    - Shorten and reinstall existing linear copper ground bar adjacent to the fume hood.

    - Provide (3) new dedicated 20A circuits/receptacles for NIST equipment in the fume hood.

    - Provide and install new connections to existing rooftop lightning protection system to new exhaust fan and exhaust fan stack to maintain UL listing of building lightning protection system. Contractor performing work shall be a licensed lightning protection contractor and provide updated UL lighting protection system certification.

    - Bond fume hood, exhaust piping and exhaust fan per equipment manufacturer’s specifications.

  - Fire Alarm/BMS

    - Provide and install Fume hood panic alarm system consisting of push button, audible and visual alarms, supervised by the building fire alarm panel. Panic alarm system shall be reviewed and approved by NIST Fire Protection Authority Division (FPAD).

Task 02 – Safety on the NIST Campus

See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

Task 03 – Safety-Related Equipment

See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

Task 04– Training

See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

Task 05– Health Hazard Assessments and Medical Evaluations

See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

Task 06 – Homeland Security Presidential Directive (HSPD)-12

See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

POSITION SENSITIVITY DESIGNATIONS REQUIREMENT

See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

INSPECTIONS & ACEPTANCE

In addition to the inspection and acceptance terms articulated in the specific FAR clause that allows the Government reserves the right to perform such performance tests and evaluations as defined below to verify specified system performance. Such tests and evaluations, if performed, shall be conducted within the environment that the system is to be operated. The Contractor has the right to be present during the tests and evaluations, if performed, at the Contractor’s expense.

PERFORMANCE TESTS:

- Specific Tests: Hood and exhaust fan will be tested to ASHRAE 110 specifications by Contractor.  A report shall be submitted to the government for review and acceptance.

Ownership of the equipment shall transfer to NIST upon acceptance of project completion by the Government.

The Government will test, inspect, and accept or reject the equipment within 10 working of the receipt of the equipment unless otherwise indicated above. The Government reserves the right to conduct quality assurance testing to confirm that a given instrument(s) meets the manufacturer’s and/or the Government’s performance specifications. It is anticipated that the equipment will meet all manufacturer’s specifications and/or the Government’s performance specifications identified in the most recent operations and maintenance manual for each piece of equipment and/or in this document.

# PART 3: CONSTRUCTION DRAWINGS AND SPECIFICATIONS

- Refer to attached construction drawings and specifications.

- Refer to NIST’s Site Standard Specifications attachment for information and requirements.

- REQUIREMENTS FOR CONTRACTOR PERSONNEL

SAFETY:  The Contractor employee must be responsible for knowing and complying with Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

SECURITY:  See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

IDENTIFICATION BADGES:  The Contractor employee must be responsible for knowing and complying with Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

V.  SCHEDULE OF DELIVERABLES

Preliminary Construction Schedule

Contractor shall provide a preliminary construction schedule in the form of a Gantt chart with the minimum milestones:

| Preliminary Construction Schedule Milestones |  |
| --- | --- |
| 1 | Mobilization |
| 2 | Submittal review, including delegated design submittals |
| 3 | Equipment delivery dates |
| 4 | Major equipment installation days |
| 5 | Stairwell closures and impairments |
| 6 | Anticipated utility outages |
| 7 | Commissioning, testing, and acceptance |
| 8 | NIST user Training |
| 9 | Close out |

Construction Submittals

Contractor shall provide the following submittals to the COR for Government approval:

| Division | Submittal Description |
| --- | --- |
| 00 | Procurement and Contracting Requirement |
| 01 | General Requirements |
| 02 | Existing Conditions |
| 03 | Concrete |
| 07 | Thermal and Moisture Protection |
| 08 | Openings |
| 09 | Finishes |
| 10 | Specialties |
| 11 | Equipment |
| 23 | HVAC |
| 26 | Electrical |
| 27 | Telecommunications |

- Submittals shall be provided through a NIST-approved, secure electronic site accessible by NIST.

- Quality Control Plans and Site-Specific Safety Plans shall be submitted no later than 30 days after award.

- The Contractor shall allow for the following NIST review periods and shall incorporate the review times into the project schedule. Listed review times do not account for holidays. All reviews listed below may not be required for every project.

The contractor shall allow for the following NIST review periods and incorporate them into the project schedule. The listed review times do not account for holidays that may occur during the week.

| REVIEW TYPE | BUSINESS DAYS REQUIRED BY NIST FOR REVIEW |
| --- | --- |
| Construction Submittals | 10 |
| Delegate Design Submittals | 10 |
| Requests for Information (RFIs) | 10 |
| NIST Boulder Safety Health and Environment Division (BSHED) | 10 |
| NIST Safety | 10 |
| NIST Security (ESO) | 10 |

STANDARDS OF ACCEPTANCE: See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

VI. PAYMENT SCHEDULE

See FAR 52.232-5, Payments under Fixed-Price Construction Contracts.

- SITE MOBILIZATION

See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

- SECURITY REQUIREMENTS

See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

- IT REQUIREMENTS

See Attachment 1 - NIST Boulder General Contractor Requirements – Rev C, included in the contract for information on rules and requirements of performing work on the National Institute of Standards and Technology (NIST) sites in Boulder and Ft. Collins, Colorado.

- ATTACHMENTS:

- 01A NIST Boulder General Contractor Requirements - Rev C

- Design Drawings

- Design Specifications