# Performance Work Statement

# for

# Operations & Maintenance

# for the

# Business Operations Center

Version 10

03 March 2026

# Part 1

# General Information

The Contractor shall provide personnel to perform services as defined in this Performance Work Statement (PWS) for the U.S. Department of Labor (DOL), heretofore known as “the Government” in support of the tasks defined herein.

## Description of Services / Introduction

The Contractor shall provide all personnel, equipment, tools, materials, supervision, and other items and non-personal services necessary to perform building Operations and Maintenance (O&M) services at the Frances Perkins Building (FPB) as defined in this PWS, except as specified in Part 3 as government furnished property and services. DOL requires O&M services for the safety and protection of all assigned personnel, visitors, and guests that frequent the FPB.

The Contractor shall perform to the standards in this contract action. This is a non-personnel services contract, and the Government shall not exercise any supervision or control over the contracted service providers performing the services herein. Contract service providers shall be accountable solely to the Contractor who, in turn is responsible to the Government.

The following sections detail the DOL minimum requirements and acceptable outcomes. The Contractor shall closely monitor all aspects of the work, identify deficiencies, and implement corrective action, without reliance on Government oversight. To the extent possible and consistent with Executive Order (EO) 13788, the Contractor shall maximize the use of goods, products, and materials that are produced in the United States.

## Background

The Business Operations Center (BOC) supports and enables DOL agencies in fulfilling their missions by providing transparent and customer-focused business operations services. BOC provides leadership and guidance in employee safety and occupational health, workers' compensation services, mail management, facilities and real property management, personal property management, fleet and sustainability management, and library and information services. BOC also provides direct customer service support for DOL programs and employees located in the FPB.

The FPB is the national headquarters for the DOL. The FPB is situated on approximately 15 acres of land at 200 Constitution Ave. NW, Washington, DC  20210 and is approximately 1.8 million gross square / 925,000 usable square feet with the capacity for over 5,500 employees. The building includes four garages with approximately 1,000 parking spaces, as well as amenities including a cafeteria, coffee shop, snack bar, fitness center, dry cleaner, child development center (CDC), credit union, and post office.

DOL is currently in need of a high-quality experienced Contractor to provide all labor, supervision, transportation, equipment, safety, supplies and materials (except those supplies and materials (if any) designated as Government-furnished) and incidentals necessary to complete the O&M service requirements.

## Objectives

The objective of this contract action is to obtain efficient, effective, mission-focused, high-quality facilities operations, maintenance, repair, and remediation services that will meet the current and future needs of DOL over the term of the BPA. This includes not only the accomplishment of predefined tasks, but also the technical, managerial, and decision-making expertise of a Contractor to manage O&M of the facility, customer requests, and projects in partnership with DOL.

## Scope

The Contractor shall provide all personnel, equipment, tools, materials, supervision, and other items and non-personal services to obtain efficient, effective, mission-focused, high-quality facilities operations, maintenance, repair, and remediation services within the property line of 200 Constitution Ave. NW, Washington, DC 20210, including:

- All electrical systems, low voltage (<600V), high voltage (5kV class and 15kV class), interior and exterior lighting, and related equipment.

- Mechanical, plumbing, heating, ventilation, and air conditioning (HVAC) systems, refrigeration, and equipment.

- Fire protection and life safety systems and equipment.

- All building controls and control systems.

- Architectural, decorative, and structural systems, fixtures, and equipment within the site to the property line.

- On-site service desk with operations from 6:00am to 6:00pm, Monday through Friday, except holidays per paragraph 1.6.4.

- Recordkeeping and work order management using the government furnished computerized maintenance management system (CMMS) ServiceNow, and related administrative functions.

- Door hardware, lock, and keying services, access and perimeter control systems, except those systems (or portions thereof) explicitly identified as owned or operated by a tenant agency. Maintaining and enforcing master key systems, including pinning diagrams. Scope includes all locks in the building including all building exterior, hallway, and interior doors, cabinetry, desks, systems furniture, and file cabinets. Includes picking locks, as necessary, when keys are lost or unavailable, and re-keying/re-coring/replacing locksets where keys are lost or unavailable.

- Dock levelers, garage doors, parking control equipment, rolling doors, conference room partitions, and guard booths.

- Procurement, installation, maintenance, and replacement of all building and restroom dispensers (toilet paper, hand towel, soap, and hand sanitizer). Excludes purchase or restocking of paper towels, toilet paper, soap, or hand sanitizer that is provided and restocked by the separate custodial contractor.

- Static and dynamic bollard, wedge and barrier systems, including motorized barriers and gates.

- All concessions, pantry, kitchenette, cafeteria, coffee bar, and kitchen area equipment. Permanently installed HVAC, refrigeration, and plumbing equipment. Kitchen appliances, grease traps, exhaust hoods and ducts, exhaust hood cleaning systems, general cafeteria equipment, and fire suppression and alarm equipment and systems. All food service equipment connected to utilities whether permanently installed or movable (e.g., steamers, ovens, reach-in refrigerators/freezers, ice makers, coffee makers). Recurring food service equipment water filter replacement per manufacturer’s recommendations. Recurring grease trap cleaning and exhaust hood cleaning per applicable code requirements.

- Roofing systems.

- Stormwater Management.

- Mechanical equipment for all anchor points, fall protection, and window washing systems, (wall glider, tracks, davits, pedestals, and associated equipment)

- US and DOL flagpoles, lighting and pulley systems.

- Elevator operation, maintenance, and repair.

- Mold remediation, restoration, and testing services.

- Hazardous material, asbestos testing/abatement, and assessment services.

- Equipment, maintenance, certification, and inspection services. Preventive maintenance, corrective maintenance, repair, and certification of government-owned material handling equipment and personnel lifts.

- Repair and alteration construction.

- Condition assessments and system surveys.

- Preventative, scheduled, and unscheduled maintenance.

- 24-hour per day / 7 days per week emergency response services.

- Building Automation System (BAS) monitoring, operation, optimization, maintenance, configuration, update, and related services.

- Miscellaneous building / maintenance services to assist with the day-to-day facility operations, including but not limited to: cleaning  and replacing vents and filters; adjusting climate conditions; door adjustments and lockouts; hanging pictures/banners/plaques; installing wall mounted whiteboards; installing TVs and their mounting brackets; replacing damaged or stained ceiling tiles, making minor modifications to spaces such as installing electrical outlets (not more than 2 outlets or switches per service request); installing electrical whips for systems furniture; replacing damaged or stained carpet tiles.

- Installing temporary leak umbrellas in the ceiling and placing the ceiling tiles (or drywall) back in place within 48 hours of the initial umbrella installation. Monitoring and adjusting umbrella as necessary to prevent damage. Emptying and replacing catch buckets.

- Regular recurring replacement of water filters on end user equipment, including, but not limited to, coffee makers and other kitchen equipment, water fountains, and drinking water chillers per manufacturer’s instructions.

- Modular and stand-alone furniture repairs, including, but not limited to assembling chairs, assembling desks, installing / removing / adjusting keyboard trays and monitor stands, reinstalling drawers, and making repairs to the office furniture as needed to restore back to a functioning state.

- Placing the building fire alarm panel in/out of service and providing fire watch as necessary to support Contractor’s work.

- Proper disposal of refrigerant containing equipment (refrigerators, freezers, small (<5 ton) HVAC units, etc.).

- CDC and other facility water testing per General Services Administration (GSA) regulations or other legal requirements.

- Emergency power generators, load banks, controls, transfer switches, and electrical equipment. Emergency power fuel storage tanks, pipes, and ancillary systems.

- Government furnished items are specifically excluded in this contract, except as specified.

## Period of Performance

The anticipated period of performance shall be for one (1) Base Period of 12 months and four (4) 12-month option periods. The Period of Performance reads as follows:

Base Period:  	March 1, 2027 – February 29, 2028

Option Period I:  	March 1, 2028 – February 28, 2029

Option Period II:  	March 1, 2029 – February 28, 2030

Option Period III:  	March 1, 2030 – February 28, 2031

Option Period IV: 	March 1, 2031 – February 29, 2032

The government reserves the right to extend the term of this contract action at the prices set forth in Section B in accordance with the terms and conditions contained in Federal Acquisition Regulation (FAR) 52.217-9 entitled, “Option to Extend the Term of the Contract.”

## General Information

### 1.6.1	Quality Control

The Contractor shall develop and maintain an effective quality control program to ensure services are performed in accordance with this PWS. The Contractor shall develop and implement procedures to identify, prevent, and ensure non-recurrence of defective services. The Contractor’s quality control program is the means by which he assures himself that his work complies with the requirement of the contract. As a minimum, the Contractor shall develop quality control procedures that address the areas identified in Technical Exhibit 1, “Performance Requirements Summary”. After acceptance of the Quality Control Plan, the Contractor shall receive the Contracting Officer’s (CO’s) acceptance in writing of any proposed change to his QC system. The Contractor shall submit the Quality Control Plan (QCP) as a stand-alone attachment not subject to the page restrictions of the Technical Proposal. The revised QCP is to be submitted for review and approval to the CO or designee within 30 calendar days of Contract start date.

The initial Quality Control Plan shall be delivered with the Contractor’s proposal.

### 1.6.2	Quality Assurance

The government shall evaluate the Contractor’s performance under this contract action in accordance with the Quality Assurance Surveillance Plan (QASP). This plan is primarily focused on what the government must do to ensure that the Contractor has performed in accordance with the performance standards. It defines how the performance standards will be applied, the frequency of surveillance, and the minimum acceptable defect rates.

As part of the Government’s quality assurance program, the Government may:

- Review and, if warranted, reject any reports or other submittals required from the Contractor.

- Review performance and service records, including monthly progress reports, BAS data, CMMS data, and any computerized or hard copy records maintained by the Contractor documenting performance under this Contract, and require correction of any unsatisfactory conditions noted.

- Determine the adequacy of the Contractor’s QCP and documentation and the overall success of this program. The Government shall order improvements, if it determines the program is insufficient or ineffective.

- Obtain tenant satisfaction and CMMS survey information and require improvements in service on the basis of such information to the extent such results correlate with deficiencies in Contract requirements.

- Conduct physical inspections of facility equipment and systems, including programs and files maintained on computers in Contractor onsite offices and work areas, and require correction of deficiencies noted.

- Perform inspections with Government personnel or independent third-party inspectors.

### 1.6.3	Government Remedies

The Contracting Officer shall follow FAR 52.212-4, “Contract Terms and Conditions-Commercial Items” or 52.246-4, “Inspection of Services-Fixed Price” for Contractor’s failure to perform satisfactory services or failure to correct non-conforming services.

### 1.6.4	Recognized Holidays

The Contractor is not required to perform regular scheduled services on the following U.S. holidays, but will be available and respond in the event of an emergency:

New Year’s Day	Labor Day

Martin Luther King Jr.’s Birthday	Columbus Day

President’s Day	Veteran’s Day

Memorial Day	Thanksgiving Day

Juneteenth Day	Christmas Day

Independence Day

### 1.6.5	Hours of Operation

The Contractor shall perform during the normal duty hours of 6:00am to 6:00pm, Monday thru Friday, except holidays per paragraph 1.6.4. During administrative closings (e.g., Presidential Executive Order, weather related closure) or similar government directed facility closings, the Contractor will conduct work unless directed otherwise by the CO or the CO’s designated Contracting Officer’s Representative (COR). The Contractor shall at all times maintain an adequate workforce for the uninterrupted performance of all tasks defined within this performance work statement. Telecommuting or “work at home” is not authorized under this contract action unless under emergency situations as determined by the COR.

### 1.6.6	Place of Performance

The work to be performed under this contract action will be performed at the U.S. Department of Labor’s Frances Perkins Building, 200 Constitution Ave. NW, Washington, DC 20210.

### 1.6.7	Type of Contract

The government anticipates award of a Blanket Purchase Agreement (BPA) with fixed labor rates. Orders issued under this Blanket Purchase Agreement may be on a firm-fixed price, labor hours, and/or time and materials basis.

### 1.6.8	Security Requirements

#### 1.6.8.1	Personal Identity Verification (PIV) of Contracted Personnel

The Contractor shall comply with agency personal identity verification procedures that implement Homeland Security Presidential Directive-12 (HSPD-12), Office of Management and Budget (OMB) guidance M-05-24, and Federal Information Processing Standards Publication (FIPS PUB) Number 201.

The Contractor shall insert these security requirements in all subcontracts when the subcontractor is required to have routine physical access to a Federally controlled facility and/or routine access to a Federally controlled information system.

The CO may delay final payment if the Contractor fails to comply with these requirements.

The Contractor shall ensure that all identification issued under this PWS (whether to a prime or subcontractor employee) is returned to the issuing agency unless otherwise approved in writing by the COR: When no longer needed for contract performance; Upon completion of the Contractor employee's employment; or Upon contract completion or termination.

The Contractor shall notify the Government when Credentials are lost. In that event, the Contractor will be responsible for reimbursing the Government for its cost in issuing a replacement Credential. An incident report may be required prior to the issuance of a replacement Credential.

All Contractor personnel requiring facility or IT system access, may be required to fill out and submit security HSPD-12 forms and fingerprint cards prior to being allowed access. The COR or designee will provide detailed instructions on the HSPD-12 process, the forms to be submitted, and the handling of the forms after the PWS or individual order has been awarded. Unless otherwise indicated at the call order level or granted an extension by the CO, security forms shall be submitted to the COR within seven calendar days of award.

The Government, at its sole discretion, may grant temporary suitability determinations to Regular or Temporary Employees. However, the granting of a temporary suitability determination to any such employee shall not be considered as assurance that a favorable suitability determination will follow.

Only Contractor personnel permanently assigned to the FPB (i.e., 40 hours/week) under this contract will be issued a PIV by DOL. Permanently assigned personnel may receive escort privileges and unescorted access privileges to the FPB at the discretion of the COR, or designee, and with approval from Security Center. No additional Contractor personnel will be issued a DOL PIV, regardless of how often they visit FPB and will not be allowed access to FPB regardless of whether they have a PIV or other government identification from GSA or another federal agency. Any additional Contractor personnel wanting access to FPB to perform a task under this contract shall request approval for access from the COR, or designee, 48 hours prior to the proposed visit.

#### 1.6.8.2	Physical Security

The Contractor shall be responsible for safeguarding all Government property provided for Contractor use in accordance with the Government Property (GP) clause, FAR 52.245-1. Any loss of integrity in the lock and keying system shall be immediately reported to the COR.

#### 1.6.8.3	Key Control

The Contractor shall follow the building’s key control program. Refer to Policy 5900.1A ADM, Physical Access Control Systems (PACS) in GSA-Controlled Space. Keys issued to the Contractor or the Contractor’s personnel, or subcontractors shall be signed for and not transferred to other personnel unless recorded in the key control log. All new locks shall be incorporated into existing grand master key system. The Contractor shall develop procedures covering key control that shall be included in the QC plan. Providing keys for tenants is non-reimbursable. The Contractor shall be financially liable and shall furnish locksmith services and key blanks for installation and removal of locksets and tumblers, and costs associated with re-keying due to the loss of a master key by Contractor or subcontractor.  The Contractor shall also be financially responsible for duplication of keys, replacement of locksets, opening doors in the event of lost keys by employees or subcontractors, and replacement of keys and locksets, due to keys not being recovered from terminated employees or subcontractors. The Contractor shall immediately report any occurrences of lost or duplicated keys to the COR.

#### 1.6.8.4	Lost Keys

In the event keys, other than master keys, are lost or duplicated, the Contractor shall, upon direction of the COR, re-key or replace the affected lock or locks. The government, at its option, may replace the affected lock or locks or perform re-keying. When the government performs the replacement of locks or rekeying or locks, the total cost of re-keying or the replacement of the lock shall be deducted from the monthly payment due the Contractor. In the event a master key is lost or duplicated, the government shall replace all locks and keys for that system and the total cost deducted from the monthly payment due the Contractor.

#### 1.6.8.5	Key Use

The Contractor shall prohibit the use of government issued keys and key cards by any persons other than the Contractor’s employees. The Contractor shall prohibit the opening of locked areas by Contractor employees to permit entrance of persons other than Contractor employees engaged in the performance of assigned work in those areas, or personnel authorized entrance by the COR.

#### 1.6.8.6	Lock Combinations

The Contractor shall ensure lock combinations are appropriately safeguarded. As directed by the government, the contractor shall maintain/repair combination locks, reset/change lock combinations, install/remove combination locks, and open combination locks when the combination has been lost.

### 1.6.9	Special Qualifications

The Contractor is responsible for ensuring all employees possess all licenses and certifications required in the execution of this contract action, including licenses to operate government-furnished material handling equipment, personnel lifts, and any rental equipment required to perform work under this PWS.

### 1.6.10	Post Award Conference / Periodic Progress Meetings

The Contractor agrees to attend any post award conference convened by the contracting activity or contract administration office in accordance with FAR Subpart 42.5. The CO, COR, and other government personnel, as appropriate, may meet periodically with the Contractor to review the Contractor's performance. At these meetings, the CO will apprise the Contractor of how the government views the Contractor's performance and the Contractor will apprise the government of problems, if any, being experienced. Appropriate action shall be taken to resolve outstanding issues. These meetings shall be at no additional cost to the government.

### 1.6.11	Contracting Officer’s Representative

A COR will be delegated separately.

### 1.6.12	Staffing

The Contractor shall adhere to the submitted staffing plan and subcontracting plan that was submitted prior to award as part of the bid proposal. Contractor shall submit staffing / subcontractor plan that provides enough staff at the various levels of expertise to ensure all scheduled and unscheduled services are performed and conditions are maintained to avoid any disruption to the tenant. Only the personnel listed on the Contractor’s staffing plan will be allowed to work under this contract (i.e., if there are ten people listed on the staffing plan with the names A, B, C, D, E, F, G, H, I, and J, then only A, B, C, D, E, F, G, H, I, and J will be allowed to perform work under the contract). Any changes to the proposed staffing levels, qualifications of proposed staff or key personnel, or the areas of expertise or disciplines of the proposed staff, shall be submitted for review and approval from the CO or their designee before any changes can be made. The contractor shall maintain an accurate up-to-date staffing plan and shall provide the document to the government within 24 hours of any change.

### 1.6.13	Key Personnel

The following personnel are considered Key Personnel by the government: Project Manager, Alternate Project Manager, Onsite Supervisor, Alternate Onsite Supervisor, and Safety Manager. The Contractor shall designate Key Personnel in writing and shall not change Key Personnel without approval of the CO or COR. Qualifications for all Key Personnel are listed below. Submit Key Personnel resumes for COR approval not later than 14 calendar days before contract start.

#### 1.6.13.1	Project Manager

The Contractor shall provide a Project Manager who shall be responsible for the performance of the work under this contract. The Alternate Project Manager shall act for the Contractor when the Project Manager is absent. The Project Manager and Alternate Project Manager shall have full authority to act for the Contractor on all matters relating to this contract action. They shall have the authority to accept notices of deductions, inspection reports, and all other correspondence on behalf of the Contractor. The Project Manager or Alternate Project Manager shall be onsite during normal contract duty hours and available 24/7/365 by phone, email, and text. The Project Manager shall attend meetings with the government as directed by the CO or COR.

The Project Manager shall have five years of experience, within the last ten years, as a Project Manager in facility operations and maintenance, management, and supervision in buildings of the approximate size, complexity, and characteristics of the FPB. New and replacement project managers shall meet these qualification standards. The Project Manager and Alternate Project Manager resumes shall contain a detailed description of their last five years’ applicable employment history, including names and addresses of the companies they worked for and names and contact information for their immediate supervisors.

#### 1.6.13.2	Onsite Supervisor

The Onsite Supervisor shall be responsible for the performance of work and supervision of Contractor personnel. The Onsite Supervisor will have direct authority over all Contractor personnel performing work. The Onsite Supervisor shall be capable of identifying existing and predictable hazards in the surroundings or working conditions which are unsanitary, hazardous, or dangerous to employees, and shall take prompt corrective measures to eliminate the hazards. The Onsite Supervisor, or the Alternate Onsite Supervisor when the Onsite Supervisor is absent, shall be onsite during normal contract duty hours. The Onsite Supervisor shall possess at least five years of experience, within the last ten years, in directing operation and maintenance of equipment in a supervisory capacity for equipment of the approximate size, complexity, and other characteristics of the equipment in the FPB. Both new and replacement Onsite Supervisors shall meet these qualification standards. The Onsite Supervisor and Alternate Onsite Supervisor shall be experienced, certified and licensed in the maintenance of complex facilities and in the operation of utility systems of the type used at the FPB. Supervisory personnel shall be experienced in the administration, scheduling, and coordination of a work force for maintenance of a facility comparable to the FPB. The Onsite Supervisor and Alternate Onsite Supervisor resumes shall contain a detailed description of their last five years’ applicable employment history, including names and addresses of the companies they worked for and names and contact information for their immediate supervisors.

#### 1.6.13.3	Safety Manager

The Contractor shall appoint a Safety Manager which may be a collateral duty. Safety managers shall have responsibility for all aspects of requirement for the Contractor personnel working at FPB, Contractor’s equipment, Contractor’s safety training, safety compliance, Contractor’s safety reports, and other conditions as needed. The Safety Manager’s resume shall contain a detailed description of their last five years’ applicable employment history, including names and addresses of the companies they worked for and names and contact information for their immediate supervisors.

### 1.6.14	Personnel

Submit resumes for COR approval not later than 14 calendar days before contract start for all positions in this section.

#### 1.6.14.1	Fire Alarm System Technician

Fire alarm systems technicians performing contract work must meet the service personnel qualification requirements in the current edition of National Fire Protection Association (NFPA) 72 and hold at least a National Institute for Certification in Engineering Technologies (NICET) Level 2 (Associate Engineering Technician) in Fire Protection Engineering Technology, Fire Alarm Systems. Additionally, the technician must have experience in the past five (5) years performing fire alarm system testing, repair, maintenance, installation, sprinkler-head replacement, placing the building fire alarm system in by-pass, and related activities for buildings and equipment comparable to the buildings and equipment covered by this PWS.

Technicians modifying the fire alarm control panel of systems must be factory trained and currently certified for the operating system, including software version, of the fire alarm system and must provide documentation of this certification to the COR. The Contractor shall provide documentation to the COR within ten days of award on qualifications identified by this standard.

#### 1.6.14.2	BAS Technician

The Contractor shall ensure all personnel involved in the operation, adjustment, and/or maintenance of all BAS are factory trained and certified by the manufacturer of the system. The Contractor shall provide to the COR documentation of the level of experience, including any certificates of training for all employees who will be involved in this function. Technicians modifying BAS systems shall be factory trained and currently certified for the operating system, including software version, of the BAS and shall provide documentation of the certification to the COR. The Contractor shall provide documentation to the COR within ten days of award on qualifications identified in this standard.

#### 1.6.14.3	Journeyman Electrician

The Contractor shall ensure all Journeyman Electricians possess a journeyman card and have a minimum of five years of experience in the trade. They must be able to independently determine appropriate work methods per applicable codes and craft techniques necessary to accomplish work assignments and be capable of performing a variety of electrical services. The nature of the work assignments will cover a broad range of preventive maintenance, repairs, replacements, and installations or electrical equipment <600 volts and up to 600 amps. The Contractor shall provide documentation to the COR within ten days of award on qualifications identified in this standard.

#### 1.6.14.4	Journeyman HVAC Technician

The Contractor shall have all Journeyman HVAC Technicians possess a journeyman card with universal certifications and have a minimum of five years of experience working in the trade. All HVAC personnel shall perform a wide variety of routine preventive maintenance and mechanical repairs on heating, cooling, refrigeration, plumbing (including removing/installing insulation) and related equipment in the facility. These individuals must have knowledge of the Principles and Theories of Air Conditioning and Refrigeration Systems and large mechanical infrastructures to include plumbing, pipefitting, heating and cooling systems, knowledge/use of the accepted practices, processes, materials, and tools of the facility. The Contractor shall provide documentation to the COR within ten days of award on qualifications identified in this standard.

#### 1.6.14.5	Cafeteria Equipment Technician

The Contractor shall have all cafeteria technician possess a journeyman card and have a minimum of five years of experience in the trade. A cafeteria equipment technician must be able to install, maintain, and repair commercial kitchen equipment, including gas, electric, and refrigeration systems. Key responsibilities include diagnosing and fixing equipment malfunctions, performing preventative maintenance, and ensuring systems like ovens, fryers, and dishwashers run efficiently. This role typically requires a high school diploma, professional training at a recognized school, mechanical aptitude, and basic knowledge of electrical, plumbing, or HVAC systems.

#### 1.6.14.6	Journeyman Plumber

The Contractor shall have all Journeyman Plumbers possess a journeyman card for the plumbing trade and have a minimum of five years of experience working in the trade. The individual shall be able to independently determine the appropriate work methods and craft techniques necessary to accomplish work assignments and shall be capable of performing a variety of plumbing and pipefitting services, to include replacing cast iron, black iron, steel, copper, and plastic pipe up to eight inches in diameter, including various mechanical / brazed / welded / glued fittings, valves, gauges, and related plumbing component. Personnel shall be able to remove and replace pipe insulation, as necessary to accomplish plumbing tasks. The Contractor shall provide documentation to the COR within ten days of award on qualifications identified in this standard.

#### 1.6.14.7	Journeyman Elevator Mechanic

The Contractor shall have all elevator mechanics be of a journeyman status with a minimum of five years of experience working in the trade. They shall be recognized by the industry and licensed by the District of Columbia, as required to perform the work of this PWS. The Contractor shall provide documentation to the COR within ten days of award on qualifications identified in this standard.

#### 1.6.14.8	General Maintenance Mechanic

General Maintenance Mechanics must have at least three years’ experience in the last five years in operation and maintenance of equipment of approximate size, complexity, and other characteristics of the equipment in the FPB. General Maintenance Mechanics will perform major and minor facilities repairs and maintenance for all equipment and systems assigned. They must be familiar with a variety of trades, to include but not limited to plumbing, locksmithing, electrical, carpentry, masonry, painting, HVAC, and flooring. No licensing is required for General Maintenance Mechanics.

#### 1.6.14.9	Operations / Administrative Specialist

The Contractor shall have an Operations / Administrative Specialist with a minimum of three years of experience working in that field. The Operations / Administrative Specialist is responsible for providing technical and administrative support for the day-to-day operations of the work under this PWS. They shall be responsible for troubleshooting and resolving technical issues, ensuring the smooth operation of systems and processes, and providing administrative support. The Operations / Administrative Specialist shall serve as the primary ServiceNow operator for creating work orders, issuing work orders, closing work orders, managing the work order process, and providing work order reports for Contractor use. The Contractor shall, at the request of the COR, provide recurring work order status reports in the format specified by the Government.

#### 1.6.14.10	Journeyman High Voltage (HV) Electrician

The Contractor shall have a Journeyman High Voltage Electrician with a minimum of five years working in the field to install, maintain, and repair high-voltage electrical systems (above 600V up to 15kV class), including, but not limited to, transformers, switches, relays, cabling, grounding, circuit breakers, switchgear, and control equipment, focusing on safety, troubleshooting complex faults in energized systems, reading blueprints, closing and opening both energized and unenergized breakers, and ensuring compliance with electrical codes, often working indoors in all conditions with heavy equipment and specialized safety gear. Individual(s) must be able to diagnose problems, replace components (breakers, motors, wiring), perform preventative maintenance, and work from heights or underground, requiring significant physical stamina and critical thinking.

#### 1.6.14.11	Locksmith

The Contractor shall have a Locksmith with three years of experience in the field who installs, maintains, repairs, and replaces various locking mechanisms and security hardware. The Locksmith shall have experience in key duplication, rekeying, re-coring locks, troubleshooting electronic and manual access systems, and opening doors in the event of lost keys or combinations.

### 1.6.15	Training

#### 1.6.15.1	CMMS

Contractor shall ensure that all staff using ServiceNow CMMS complete the six-hour Government-provided new user training, at a minimum, covering:

- Basic Navigation

Work Order Tracking

Asset Management

Preventive Maintenance

Reports

Contractor shall identify and designate staff responsible for performing specific administrative tasks within CMMS. In addition to CMMS New User Training, designated staff shall complete CMMS Contract Administration Training for Contractors, which takes approximately three hours and covers the following at a minimum:

- Account Management

- People Records

- Labor Records

- Location Records

- Preventive Maintenance Work Orders

- Conduct Quality Control Inspections

- Generate Monthly Progress Reports

Training will be provided online. Contractor shall work with COR to accomplish training during the Phase-In period. Training shall be completed at no additional cost to the Government. Contractor shall submit written certification to the COR within five business days of completing training. Contractor may request a waiver for staff that have previously completed CMMS training and can demonstrate knowledge and proficiency using the ServiceNow system.

### 1.6.16	Reserved

### 1.6.17	Identification of Contractor Employees

All contract personnel attending meetings, answering government telephones, and working in other situations where their contractor status is not obvious to third parties are required to identify themselves as such to avoid creating an impression in the minds of members of the public that they are government officials. Contractor shall ensure that all documents or reports produced by the Contractor are suitably marked as Contractor products or that Contractor participation is appropriately disclosed. All Contractors shall utilize a DOL-standard signature block on all emails sent under this contract, including the requirement to have “(Contractor)” after their name in their signature block.

The Contractor shall require all employees wear distinctive uniform clothing for ready identification, and ensure all employees are in uniform no later than the contract start date. This requirement applies to new and replacement employees. The uniform shall have the Contractor's company name and the employee’s name affixed thereon in a permanent or semi-permanent manner such as a badge or monogram. The Contractor employees shall be in uniform while on site and always present a clean and professional appearance. Contract employees shall always wear their government-provided identification (e.g., PIV) visible above the waist while on site.

### 1.6.18	Organizational Conflict of Interest

Contractor and subcontractor personnel performing work under this contract action may receive, have access to or participate in the development of proprietary or source selection information (e.g., cost or pricing information, budget information or analyses, specifications or work statements, etc.) or perform evaluation services which may create a current or subsequent Organizational Conflict of Interests (OCI), as defined in FAR Subpart 9.5. The Contractor shall notify the CO immediately whenever it becomes aware that such access or participation may result in any actual or potential OCI and shall promptly submit a plan to the CO to avoid or mitigate any such OCI. The Contractor’s mitigation plan will be determined to be acceptable solely at the discretion of the CO and in the event the CO unilaterally determines that any such OCI cannot be satisfactorily avoided or mitigated, the CO may affect other remedies as he or she deems necessary, including prohibiting the Contractor from participation in subsequent contracted requirements which may be affected by the OCI.

### 1.6.19	Removing Employees for Misconduct or Security Reasons

The Government, may at its sole discretion, direct the Contractor to remove any Contractor employee from DOL facilities for misconduct, suitability, or security reasons. Removal does not relieve the Contractor of the responsibility to continue providing the services required under this PWS.

### 1.6.20	Scheduling Services with Other Contractors

The Government may undertake or award other contracts for additional work within the FPB. When work in the FPB is done through another contractor (“third-party contractor”), the O&M Contractor will only be required to provide administrative support which includes attending project meetings, reviewing the third-party contractor’s SOW for situational awareness only, and ensuring the new work does not pose any risk to the FPB. The O&M Contractor shall not commit or permit any act that will interfere with the performance of work by a third-party contractor or by Government employees.

All work performed by third-party contractors will be warranted by the third-party contractor. During the time that the third-party contractor warranty is in effect, the O&M Contractor will not be expected to perform any repair work that would void the third-party contractor’s warranty.

### 1.6.21	Phase-In / Phase-Out Period

#### 1.6.21.1.	Personnel

To minimize any decreases in productivity, and to prevent possible negative impacts on additional services, the Contractor shall have personnel on board during the 30-day Phase-In and Phase-Out periods. During the Phase-In period, the Contractor shall become familiar with performance requirements in order to commence full performance of services on the contract action start date. The purpose of this phase is to permit a transition that is seamless to the tenants and to assess the condition of the building and incomplete maintenance work at the time of Contractor transition.

#### 1.6.21.2	Reserved

#### 1.6.21.3	Phase-In Period Tasks

During this period, the incoming Contractor shall:

- Create and submit to the COR or designee an updated Building Operating Plan (BOP) utilizing the Government-provided template at Technical Exhibit 5.

- Inspect the condition of all equipment and systems for which the Contractor shall assume responsibility and generate an equipment condition report.

- Revalidate and provide corrections to CMMS locations and equipment inventory. Provide certification to the COR or designee that the equipment inventory is complete and accurate in the CMMS.

- Obtain the work order history from ServiceNow. Provide a consolidated list of work orders that are deferred or open and submit an action plan on completing these items.

- Review the preventive maintenance schedule in CMMS. Cross-check preventive maintenance schedules and guides used by the outgoing contractor versus the 2025 PM Guide Cards at Technical Exhibit 4. Develop or edit, as required, the preventive maintenance schedules and guides in the CMMS. The new schedules and guides shall be based off of the last time preventive maintenance was performed and in accordance with the requirements of this Contract.

- Review the current schedule of maintenance and revalidate in line with accepted proposed maintenance schedules.

- Complete the Government-furnished CMMS training.

- Submit an Initial Deficiency Report, including an itemized estimate for correcting each deficiency to the COR or designee.

#### 1.6.21.4	Phase-In Period Reports

Within the 10 business days of the Phase-In period commencement, the Contractor shall submit a work and staffing schedule to the COR or designee for the Phase-In period. This schedule shall describe on a weekly basis the work to be accomplished and the staff to be onboard. At the end of each week during the Phase-In period, the Contractor shall submit a report describing the work that was actually completed.

#### 1.6.21.5	Phase-In Inventory and Clean up

As part of the Contractor’s proposal, the Contractor shall provide a firm fixed price cost (CLIN XXXX) to inventory and clean up the following spaces: N0062, N0066 (including the mechanical room, adjacent storage rooms, foyer, and old “engineering” spaces), C0065, C0052, C0050A, C0050, C0048, Sign Shop, C0041, S0018, S0019, AHU 45 mechanical room, Three fitness center HVAC rooms, S0013, S0015 (Vault 3), S0010, S0014 (AHU 55 mechanical room), South Garage storage room, Main Mechanical Room, six storage rooms in the East Garage, Vault 4 and connected fan and plenum rooms, Metro lobby storage room, N2612/N3110 (NW mechanical room), N2709/N3711 (NE mechanical room), Six elevator machine rooms located on the roof, Two mechanical rooms located on the roof, S6220 (6th floor mechanical room), and approximately 120 electrical riser closets throughout the building, At the end of this clean up, spaces shall be clean, organized, and broom swept. Spaces shall be maintained in this clean and “broom swept” condition throughout the length of the contract. Contractor shall secure all mechanical spaces, replacing locks as necessary to ensure they are all on the “mechanical room” key and maintain mechanical spaces secured throughout the length of the contract.

Contractor shall identify and remove all parts, material, equipment, furniture, debris, trash, miscellany, and other items from these spaces. Contractor shall coordinate with COR or designee for disposal instructions. Contractors shall dispose of items directed to be disposed of by COR, or designee, under this CLIN at no additional cost to government. Contractor shall not dispose of any items in existing FPB receptacles or dumpsters. Contractor is completely responsible under this CLIN for separately contracting for disposal, including costs for disposal of any hazardous materials or hazardous waste. Contractor shall inventory, clean (as necessary), and properly store in an organized accessible manner in storage rooms in the north end of N0066 mechanical room, N0062, or C0041 all items directed to be retained by COR or designee, Contractor shall maintain the inventory and maintain the stored items in an organized accessible manner through the length of the contract. Contractor shall not store any parts, material, or equipment in any other space in FPB without approval of COR or designee.

#### 1.6.21.6	Phase-Out Period

When the Contract ends, the Contractor shall comply with FAR Clause 52.237-3 Continuity of Services. During this Phase-Out period, the Contractor shall also:

- Assist the COR or designee and incoming contractor for a seamless transition in operations and maintenance with no adverse effect on the building tenants.

Provide DOL and the incoming contractor with access to all records and official documentation (both hard copies and electronic as applicable) required by this contract.

Provide training to the incoming contractor on methods of accessing and programming the BAS and other control systems.

Show the incoming contractor where all archived programs and systems literature is maintained. On the last performance day of the contract, the Contractor shall turn over to the COR or designee all keys and identification badges or cards.

Coordinate and complete disposal, cleanup, and transfer of all materials according to applicable laws.

Provide all data records (e.g., database files, spreadsheets) relating to building systems, assets, work orders, permits, work activities, and other related matters to the COR or designee.

Provide CMMS transition services to assist transitioning between incumbent and incoming contractors.

# Part 2

# Definitions & Acronyms

Additional Services. Services that the Contractor will provide at an additional cost to the Government, to include all labor, supervision, supplies and materials specifically identified as being outside the provisions of the basic services and included in the Contractor’s overall pricing. These services may be provided during or after normal working hours. The CO will issue a separate order before work may proceed.

Approval. “Approval” means the Government has reviewed submittals, deliverables, and administrative documents (e.g., insurance certificates, installation schedules, planned utility interruptions) and has determined the documents conform to BPA requirements. Government approval shall not relieve the Contractor of responsibility for complying with Federal and District of Columbia (DC) laws and regulations.

Architectural and Structural. All building structure, envelope, building improvements and finishes, and site improvements (e.g., paving, walkways, asphalt) to the property line.

Authorized User. A person or entity that handles DOL’s Controlled Unclassified Information (CUI), has completed the required advanced CUI training, and has authorization from DOL management to designate or handle CUI.

Basic Services. The recurring requirements for which the Contractor is paid as a base price (i.e., the requirements established by the PWS and related general and administrative requirements) that do not contain provisions for separate reimbursement.

Building. A man-made structure or edifice which services are performed within or on the exterior of the formation and is intended to support or shelter any use or continuous occupancy. Used interchangeably with “facility” and “site.”

Building Automation System (BAS). The system controlling and monitoring building HVAC and possibly other systems to include all device, field, and global controllers; instrumentation; networking infrastructure; computers and peripherals; software; programming; database files; and licenses.

Building Information Modeling (BIM). An intelligent 3D model-based process that gives architecture, engineering, and construction (AEC) professionals the insight and tools to more efficiently plan, design, construct, and manage buildings and infrastructure.

Building Operating Plan (BOP). A mandatory plan that the Contractor prepares for Government approval during the Phase-In period. It describes the Contractor’s program for operating and maintaining the building, to include both normal circumstances and contingencies. The submitted plan shall be maintained in a format consistent with the Government provided template.

Computerized Maintenance Management System (CMMS). The database and application software package that automates O&M and record keeping requirements, centralizes asset management functions of building operations, and tracks work orders. The CMMS for this BPA is ServiceNow.

Consumable Parts. Parts or components that customarily require regular replacement rather than repair in a maintenance program and shall be disposed of properly. Examples include oil, grease, belts, filters, ballasts, lamps, etc. This is inclusive of any consumables (including fuel) used during day-to-day operation of a generator (e.g., exercising the generator, testing). Operation of a generator for an extended period or due to a power loss would be treated as a reimbursable expense. If the operation of the generator is caused by Contractor negligence, the Contractor shall be liable for the full cost of refueling, any other provisions notwithstanding.

Contracting Officer (CO). The Government official who has the overall responsibility for the administration of this BPA. The CO alone, without delegation, is authorized to take action on behalf of the Government to amend, modify, or deviate from the BPA terms, conditions, requirements, specifications, details and/or delivery schedules, make final decisions on disputed deductions from payments for nonperformance or unsatisfactory performance; terminate the BPA or order for convenience or default; and issue final decisions regarding BPA questions or matters under dispute. However, the CO may delegate certain other responsibilities to authorized Government representatives.

Contracting Officer’s Representative (COR). A representative from the requiring activity assigned by the CO to perform surveillance and to act as liaison to the Contractor

Controlled Unclassified Information (CUI). Information the Government creates or possesses that a law, regulation, or Government-wide policy requires or specifically permits an agency to handle by means of safeguarding or dissemination controls.

Controls and Control System. Any low-voltage control, communication, and monitoring system, including but not limited to device, field and global controllers; instrumentation; networking infrastructure; computers and peripherals; software; programming; database files; and licenses. Examples are the BAS and lighting control systems. Fire protection systems and security systems are excluded from this definition for purposes of this BPA and are defined separately. Gateway devices and mapping software and files for data interchange between a control system and a fire protection or security system are considered part of the control system.

Defective Service (Deficiencies). A unit of service that does not conform to the level of performance specified in this PWS.

Elevator. Any elevator, escalator, dumbwaiter, handicapped lift, courtroom lift, platform lift or wall glider equipment, if applicable, at the location. Used interchangeably with “vertical transportation.”

Emergency. Includes, but is not limited to, bombings, bomb threats, civil disturbances, fires, explosions, electrical failure, loss of water pressure, flooding, sanitary and sewer line stoppage, chemical and gas leaks, medical emergencies, hurricanes, tornadoes, floods, snowstorms, and earthquakes.

Emergency Callback. A request for service placed outside of normal working hours and of such a nature that response cannot wait for the resumption of the next day’s normal working hours.

Environmentally Sustainable. These are products or services that have a lesser or reduced effect on human health and the environment when compared with competing products or services that serve the same purpose. This comparison may consider raw materials acquisition, production, manufacturing, product, chemicals, packaging, distribution, reuse, operation, maintenance, or disposal of the product or service. Products that are identified as environmentally sustainable shall be selected over those which do not carry such designations.

Fire Protection and Life Safety Systems. Systems and equipment installed in the building to (1) detect fire and products of combustion, (2) notify building occupants and emergency responders, (3) initiate smoke control and management systems, (4) initiate fire suppression systems, (5) control or suppress fires, and (6) facilitate or enhance emergency egress. These systems also may communicate with other major building systems for fire and smoke control, elevator recall, and utilities control. Life safety systems and equipment include emergency lighting, exit signage, special egress door locking arrangements, and exit stair markings.

General Program. The work specified in this specification shall be in accordance with all Federal and DC laws and regulations, and shall follow the more stringent of them. The Contractor shall also follow all applicable standard industry practices.

Initial Deficiency Report. The report created by the Contractor during the Phase-In period identifying deficiencies that may exist, at BPA or order inception, in the equipment and systems covered by this PWS, as well as the Contractor's itemized price (including, but not limited to, labor, materials, overhead, and profit) for correcting each deficiency.

Maintenance Control Plan (MCP). (Elevator Maintenance Services). American Society for Mechanical Engineers (ASME) A17.1 Safety Code for Elevators and Escalators requires that all elevators be provided with a Maintenance Control Program (also referred to as a Maintenance Control Plan). A Maintenance Control Program for each unit shall be provided by the person(s) and/or firm maintaining the equipment and shall be viewable on-site by elevator personnel at all times from time of acceptance inspection and test or from the time of equipment installation or alteration.

The MCP is a written plan that details all of the maintenance tasks which shall be performed and the frequencies with which they are performed. It takes into consideration a variety of criteria, including the type of equipment, its age and condition, the type of use, environmental conditions, and any other special concerns surrounding that elevator. It is not a generic document but is intended to be a specific set of instructions designed to address all of the particular maintenance issues relating to a particular elevator. Procedures for tests; periodic inspections; maintenance; replacements; adjustments; and for traction- loss detection means, broken-suspension-member detection means, residual-strength detection means, and related circuits shall be incorporated into and made a part of the MCP. A copy of the MCP shall be located in each elevator machine room,

Miscellaneous Work. Additional labor that is performed at the request of the COR at no additional cost to the Government (i.e., part of basic services). The Contractor may also have to provide consumable materials to complete the request.

Negligence. The failure to use care under the circumstances; it is the doing of some act which a person of ordinary prudence would not have done under similar circumstances or failure to do what a person of ordinary prudence would have done under similar circumstances.

Normal Duty Hours. The hours of building operations under most circumstances when all services shall be provided to all occupants. For this contract, 6:00am to 6:00pm, Monday thru Friday, except holidays per paragraph 1.6.4.

Occupant Emergency Plan (OEP). Details what the building tenants shall do in case of an emergency. The plan identifies fire wardens, shelter in place locations, etc. The Contractor shall support all OEP efforts to the fullest extent possible.

Operations. The continual process of using building equipment systems to accomplish their function, optimize building performance, and improve energy efficiency. Operations include analysis of requirements and systems capabilities, operating controls and control systems, responding to service requests, touring and observing equipment performance and condition, adjusting equipment, identifying needed maintenance and equipment, and maintaining lubrication and chemical treatments, etc.

Predictive Maintenance. A program of maintenance activities in which scheduling of maintenance derives from monitoring the operating condition or changes in the operating condition of equipment being maintained. Predictive maintenance activities should follow performance guidelines consistent with preventive maintenance activities; the only variance is in the “trigger event.”

Preventive Maintenance. A program of maintenance activities performed based on a fixed schedule or on equipment runtimes. Also, all work performed including adjustments and procedures necessary to sustain the proper operation of all building equipment and systems pending a scheduled procedure.

Quality Assurance (QA). Those actions taken by the government to ensure services meet the requirements of the Performance Work Statement.

Quality Assurance Surveillance Plan (QASP). An organized written document specifying the surveillance methodology to be used for surveillance of Contractor performance.

Quality Control (QC). Those actions taken by a Contractor to control the performance of services so that they meet the requirements of the PWS.

Quality Control Plan (QCP). The Contractor’s complete written system for identifying and correcting deficiencies in the quality of services before the level of performance becomes unacceptable. Preparation of this document is the responsibility of the Contractor. The QCP shall be submitted for Government review and approval.

Quality Control Program. The Contractor’s system for identifying and correcting deficiencies in the quality of services before the level of performance becomes unacceptable. It includes those continuous actions taken by a Contractor to control the performance of their employees’ and subcontractors’ services so that they consistently meet the contract requirements.

Repair. An act of restoring inoperable, dysfunctional, or deteriorated equipment, systems, or material to a fully functional, non-deteriorated state, usually involving some combination of labor and replacement parts, components, or materials.

Repair (Non-Reimbursable). A repair that is the Contractor’s responsibility with no additional reimbursement from the Government, in accordance with this PWS.

Repair (Reimbursable). A repair that is reimbursable to the Contractor, in whole or in part, in accordance with this PWS.

Sequence of Operations. The control logic used to operate a system normally put into effect through a control program.

Standard Service. A service that is included in the monthly price as defined in the BPA document. Prices are to include all applicable labor, materials, supplies, training /

Tour. A scheduled walkthrough of a space by the Contractor to ensure equipment is running properly, to validate rooms are in good order without safety hazards, to satisfy tour and log requirements mandated by law, regulation, or this PWS, and to make any necessary adjustments to equipment operations. A tour may also involve a combination of such physical visits in addition to using automated systems for the monitoring of equipment and systems.

Vandalism. Willful and malicious destruction of property.

Warranted as Presented. The presenter guarantees the report or item presented as being accurate and truthful.

Watch. Executing tasks required for the operation of central HVAC equipment, boilers, compressors, and related equipment in a centralized location. Includes, but are not limited to starting equipment, checking at designated intervals all operating equipment in the area, recording readings, shifting equipment and loads, making adjustments at the central control center, taking water samples, making tests, and adding chemicals as required.

Work Order. A response to a tenant or agency request or a response to an observation that some equipment, system, or material covered by this BPA is inoperable, dysfunctional, deteriorated, not within normal operating parameters, or that performance standards of the BPA are not being met. Includes analysis of the problem and adjustment of operating or monitoring controls or other immediate corrective action. A requirement to perform a repair may result from the analysis stage of a work order. Work Orders may be generated automatically from interfaces to BAS or diagnostic software, by users, or by Contractor personnel. Work Orders are standard service requirements to execute a task in this PWS. Used interchangeably with “work request,” “service order,” “service request,” and similar terms. All Work Orders are entered, tracked, reported, and closed in the CMMS, ServiceNow.

# Part 3

# Government Furnished Property, Equipment, and Services

## General

The government will provide the facilities, equipment, materials, and/or services listed below. The Contractor may use space in the building and furnishings, including locker rooms and lockers (not a part of any tenant rentable or commonly accessible areas) if available with permission from the CO or designee. Any existing equipment within DOL space, such as lockers, tables, benches, chairs, and appliances may be used by the Contractor during the term of the contract, provided written authorization is received from the CO or the designee. Space in the building, furniture and furnishings, and equipment for Contractor use (including a supervisor's office) is to be used for official business only in the performance of this contract. Government-supplied telephones, laptops, tablets, radios, or other electronic equipment shall only be used for communication related to this contract. Allocated space, furnishings, and equipment shall be kept neat and clean and returned to the Government at the expiration of the contract in reasonably the same condition as at the time of entering into the contract.

## Equipment

The Contractor shall notify the Government if any government furnished equipment is damaged, lost, or stolen. In that event, the Contractor will be responsible for reimbursing the Government for all costs associated in issuing a replacement device.

### 3.2.1	Computers

Pending availability of funds, DOL will provide one laptop or tablet to each newly assigned Contractor employee and integrate each device into the DOL network. Contractor personnel shall obtain and maintain credentials required to maintain access to the DOL network. The computer equipment remains the property of the Government and shall be turned over to the government in good condition upon request or upon completion of the contract.

The Contractor shall use government-provided computers / laptops / tablets, government-provided network, government-provided shared drives for storage, and government-provided email accounts / addresses when conducting all work under this contract and when communicating with the government under this contract. Contractor shall not use their company / non-government email / addresses when communicating with the government under this contract.

The Contractor may request approval to use proprietary contractor-provided system hardware / software. Approval is subject to network and system testing, review, approval for connection to DOL’s network, and acceptance by the Office of the Chief Information Officer (OCIO).

### 3.2.2	Hand-held radios

Th Government will provide each Contractor employee under this contract a handheld radio for use in the operation and maintenance of the facility. The radio remains the property of the Government and shall be turned over to the government in good condition upon request or upon completion of the contract.

## Services

The Government will provide all utilities in the facility necessary for the Contractor’s performance of tasks outlined in this PWS. The Contractor shall instruct employees in utilities conservation practices. The Contractor shall develop and implement procedures to preclude the waste of utilities used by Contractor employees under this contract.

## Facilities

The government will provide office space for Contractor employes, including normal office amenities such as desks, chairs, and telephones. The government will provide space in the building for the storage of supplies and equipment that is to be used in the performance of work under this contract. The Contractor shall maintain all spaces assigned to them in a locked, secure, clean, neat, safe, and orderly condition. Contractor shall properly store all flammable or combustible liquids in a UL-rated flammable storage cabinet or room. The Government shall not be responsible for damage or loss to the Contractor's stored supplies, materials, replacement parts, or equipment. The Government retains the right to change permission for use of space and furnishings throughout the life of the contract.

# Part 4

# Contractor Furnished Items and Services

## 4.1	General

Except for those items specifically stated to be Government furnished in Part 3, the Contractor shall furnish all labor, services, supplies, material, and equipment necessary to perform efficiently and effectively the requirements of this Contract.

At the expiration or termination of this Contract, all equipment furnished and installed by the Contractor in the building shall remain and become the property of the Government. All material and equipment purchased by the Contractor under this Contract but not yet installed (e.g., attic stock, shop stock) shall remain in place and become the property of the Government. All electronic data used to operate, track, and maintain the facility remains the property of the Government and shall be turned over to the Government in an electronic media identified by the Government. All non-electronic media used to operate, track, and maintain the facility remains the property of the Government and shall be turned over to the Government in good condition upon request or upon the completion of the Contract.

The Contractor shall provide Contractor employees with portable electronic means (inclusive of voice, text, email, and internet) to communicate with the Government and other Contractor employees outside of normal duty hours. The Contractor shall develop procedures to communicate with the Government in order to respond to emergencies outside normal duty hours and shall provide those procedures and contact information (including alternate backup contact information) to the Government during the Phase-In period and maintain updated as necessary.

## 4.2	Clearance

See paragraph 1.6.8.

# Part 5

# Specific Tasks

The Contractor shall provide building operations and maintenance services for all systems covered by this Contract, maintain uninterrupted utilities services, provide appropriate climate control for building occupants during normal duty hours and at other times as described in this PWS, maintain or enhance energy savings established by Energy Savings Performance Contract (ESPC) or Utility Energy Savings Contract (UESC) to preserve the asset value of the facility and its systems, and minimize operating costs to the Government without compromising other Contract objectives or requirements.

## 5.1	Tenant Environment

The Contractor shall meet ASHRAE Standard 55-2017 (or latest version), Thermal Environmental Conditions for Human Occupancy, and ASHRAE 62.1-2016 (or latest version), Ventilation for Acceptable Indoor Air, throughout the normal duty hours in occupied spaces. Equipment startup shall occur efficiently to attain fully environmental conditions at the beginning of normal duty hours. The Contractor shall operate and maintain HVAC systems to achieve temperatures between 68F and 74F in cooling season and between 70F and 76F in heating season. Contractor shall maintain relative humidity between 30% and 60%.

## 5.2	Tenant Furniture

Tenant agency furniture and office equipment in the immediate vicinity of an area where the Contractor is working shall be moved and/or protected. To move tenant’s furniture and equipment, the Contractor shall submit a DL7070 request (or equivalent, if superseded) to the Movers. Contractor shall notify the COR, or designee, any time moving services are utilized. If the Contractor's work does not allow furniture and office equipment to be replaced to its original location, new locations will be designated by the COR or the tenant agency representative. The Contractor is responsible for repair or replacement due to damage the Contactor causes during Contractor’s work.

## 5.3	Building Operating Plan

The Contractor shall create the BOP in Microsoft Word format and submit it for approval to the COR or designee not later than the end of the Phase-In period and annually thereafter. The Contractor shall use the Government-provided template at Technical Exhibit 5. If the Contractor fails to submit a satisfactory BOP, the Government will withhold payments until a satisfactory plan is submitted.

The Contractor shall execute the contract requirements in accordance with the approved BOP. The Contractor shall keep the BOP updated and resubmit as changes occur.

## 5.4	Equipment Inventory

Not later than the end of the Phase-in period, the Contractor shall develop the building equipment inventory. Contractor shall maintain and update the inventory through the life of the contract, including equipment labeling and maintenance records. The Contractor shall ensure accurate data in the CMMS. Significant changes in the inventory can result in a negotiated price adjustment to the contract, which must be approved in writing by the CO. Omissions in the existing inventory do not relieve the Contractor from the responsibility for the operations, maintenance, and repair of the equipment. The Contractor may request an equitable adjustment pertaining only to physical changes in building equipment which occur after the contract start date. If the Contractor-maintained inventory data does not meet contract requirements (e.g., up to date, required equipment information) the CO may take action to withhold payments. The Contractor shall submit the updated equipment inventory annually thereafter on the anniversary of the contract award date.

## 5.5	Reserved

## 5.6	Safety Management

### 5.6.1	General

The Contractor shall comply with all applicable Federal and DC laws and regulations that relate to the operation and maintenance of equipment and systems within the scope of this contract including permitting, plans, inspection, personnel safety, control of hazardous substances, certification, recordkeeping and training. Contract personnel shall wear proper contractor-provided personal protective equipment (PPE) to meet OSHA standards where required. Throughout the contract period, the Contractor shall keep current and be aware of any changes in regulations and requirements and update its operations and training as necessary.

The Contractor shall immediately correct or mitigate any recognized safety or environmental hazard. The Contractor shall notify the COR, other designated Government representative, or appropriate authority, as applicable. The Contractor shall be responsible for any fines or penalties levied by any environmental or regulatory authority resulting from its action or inaction, but not actions or inactions of a third party or the Government.

### 5.6.2	Workplace Safety and Health Program:

The Contractor shall develop a site-specific safety and health program in compliance with 29 CFR 1910 and 29 CFR 1926, and submit to the COR or designee within 30 calendar days of contract start date for review and approval. By approving the program, the Government assumes no responsibility for the Contractor’s occupational safety and health program.

### 5.6.3	Scheduling and Record Keeping

All required safety tests, certifications, permits, plans, and other procedures required in this PWS shall be scheduled and documented in CMMS.

The Contractor shall maintain copies of all tests, certifications, permits, and other required records.

### 5.6.4	Fall Protection

The Contractor shall provide fall protection equipment to its employees, and all employees shall be adequately trained in accordance with 29 CFR 1910.28 and 29 CFR 1910.29. The Contractor shall develop specific fall protection procedures for work on roofs, equipment, and other areas at elevation and submit their fall protection plan for COR approval within 30 calendar days of contract start date.

### 5.6.5	Powered Platforms

The Contractor shall inspect, test, and maintain all Government-owned powered platforms (e.g., aerial lifts, scissor lifts, forklift, pallet jack) in accordance with 29 CFR 1910.66 and provide copies of such certifications to the COR. Aerial and scissor lifts shall be inspected before each use in accordance with 29 CFR 1910.67 and the manufacturer’s specifications.

### 5.6.6	Lock Out/Tag Out

The Contractor shall comply with 29 CFR 1910.147 lock out/tag out procedures. The Contractor’s lock out/tag out procedures shall be developed and submitted to the COR or designee within 30 calendar days of contract start date. The Contractor shall communicate the lock out/tag out procedures to all employees and affected subcontractors.

### 5.6.7	Confined Spaces

The Contractor shall evaluate, identify, and label all confined spaces in accordance with 29 CFR 1910. The Contractor shall develop a confined space entry permit system for all permit-required confined spaces within 60 calendar days of contract start date.

### 5.6.8	Facility Hazards and Accidents

The Contractor is responsible for ensuring safe working conditions and identifying hazards that exist in the work environment. When the Contractor identifies any hazardous work condition, regardless of cause, the Contractor is responsible for protecting its employees from that hazard and correcting hazards under its control. The Contractor shall report to the COR all hazards that present an imminent danger. The Contractor shall submit their hazards communication plan for COR approval within 30 calendar days of contract start date and submit an updated plan on 30 September or each year of the contract.

The Contractor shall immediately report all accidents to the COR and provide copies of any accident reports to the COR.

### 5.6.9	Disruptive or Hazardous Equipment

#### 5.6.9.1	Tools

The Contractor shall not use impact tools, powder-actuated tools, or loud tools (e.g., circular saw, power chisel, reciprocating saw) during normal duty hours without COR approval. Burning or welding equipment shall be used only after obtaining a DOL Burn Permit. Compressed gas cylinders shall be stored in accordance with 29 CFR1910.101 and welding in a confined space requires specific confined space permitting requirements.

#### 5.6.9.2	Hooks, Cranes, Hoists, Chains, and Slings

The Contractor shall inspect all hooks, cranes, hoists, chains, and slings before each use and follow the inspection requirements in 29 CFR 1910.184, 29 CFR 1910.179, and ASME B30.10, as applicable. The Contractor shall remove defective items from service. The Contractor shall ensure the devices are visibly marked with their rated load.

### 5.6.10	Scheduled Disruption to Utilities, Lighting, Fire Protection & Life Safety Systems, or Space Conditioning

Except for emergencies, any work that will disrupt utilities, fire protection or life safety systems, lighting, or space conditioning for building tenants shall be scheduled and approved at least 48 hours in advance by the COR or designee.

### 5.6.11	Safety Data Sheets and Hazard Communication Plan

#### 5.6.11.1	Safety Data Sheets

The Contractor shall make Safety Data Sheets (SDS) available to its employees in accordance with 29 CFR 1910.1200 and upon request to the COR or designee.

#### 5.6.11.2	Hazard Communication Plan

The Contractor shall develop a written Hazard Communication Plan in accordance with 29 CFR 1910.1200 as part of its overall Safety and Health Program. The written plan applies to any hazardous chemical present in the area where the Contractor is working and to which the Contractor is or may be exposed to, under normal conditions of use. The plan shall include the method the Contractor will use to provide other employers that shall also be exposed to the hazardous chemicals, knowledge of the locations where the Contractor’s SDSs are kept and how access by other employers can be obtained. The Contractor shall prepare and submit a hazardous materials inventory as an appendix to the BOP and Hazardous Communication Plan. This inventory shall itemize all materials by type as sold with an SDS and include approximate quantities stored or to be stored as well as the exact locations where hazardous materials are to be stored on the premises and the date the material was stored. The inventory shall be kept current and submitted annually by September 30 of each year and at the end of the Contract.

### 5.6.12	Labeling and signage

The Contractor shall maintain the labeling of existing equipment, pipes, storage areas, containers, confined space, and workspaces as well as associated signage, in accordance with OSHA standards to ensure labels are visible and easily readable. Any equipment, pipes, and other materials, newly installed by the Contractor that require labeling and signage per OSHA standards shall be labeled immediately upon completion of the installation and maintained throughout the Contract period.

### 5.6.13	Emergency Shutdown Instructions

Emergency shutdown instructions (including contact name and telephone numbers) and tour inspection checklists and lock out/tag out procedures shall be posted by the Contractor in all mechanical rooms and electrical rooms, as applicable to the equipment in the given room. Such instructions and checklists shall be posted in an accessible and conspicuous location. All instructions and checklists shall also be stored in CMMS.

### 5.6.14	Electrical Safety

The Contractor shall comply with NFPA 70, National Electrical Code, and NFPA 70E, Standard for Electrical Safety in the Workplace, when working on or around electrical equipment or systems or switchgear equipment. The Contractor shall ensure that any and all areas restricted to qualified personnel are secured and properly labeled.

### 5.6.15 Labeling of Electrical Circuits and Panels

The labeling of all newly installed electrical circuits and panels shall be maintained up to date either in electronic format or hard copy blueprints when the Contractor adds or modifies electrical circuits. This requires the Contractor to implement and document an overall electrical safety program that meets the requirements outlined in NFPA 70E, Article 100, General Requirements for an Electrical Safety Related Work Practice. The COR will ensure that all recorded changes in electric panels completed by third-party contractors are transmitted to the Contractor to maintain the accuracy of labeling. In the event the Contractor identifies an unlabeled circuit, the Contractor shall label the circuit in accordance with NFPA 70B.

## 5.7	Environmental Management

### 5.7.1	General

The Contractor shall use to the extent practicable, the safest and most environmentally friendly products and processes available. The Contractor shall use manufacturer recommended products. Before substituting for any manufacturer's recommended product, the Contractor shall ensure any substitution is deemed safe by the equipment manufacturer. The Contractor shall be cognizant of and comply with all applicable Federal and DC laws and regulations related to building management (e.g., permitting, inspection, testing and personnel safety, control of hazardous substances, and certification) including those related to materials and associated systems used or removed in the performance of this Contract. The Contractor shall be responsible for any fines or penalties levied by any environmental or regulatory authority resulting from its action or inaction but not resulting from the actions or inactions of a third-party or the Federal Government. The Contractor’s maintenance, operations, materials, and processes must use green products and processes including products containing recycled content, environmentally sustainable products and services, bio-based products, and products and services that minimize the use of energy, water, and other resources. All required safety and environmental tests, certifications, permits, and other procedures required in this PWS shall be scheduled in the CMMS.

### 5.7.2	Refrigerants and Refrigerators

Refrigerants are just one aspect of many building assets used to protect electronic equipment, dry compressed air, and provide tenant comfort. Refrigerants also may be considered by the U.S. Environmental Protection Agency (EPA) as Ozone Depleting Substances or contributors to Green House Gasses. The Contractor will closely monitor the refrigerant inventory, monitoring refrigerant additions to assets, establishing leak rates, performing leak inspections, and recording all data and findings in CMMS. The Contractor shall meet the requirements of the GSA Public Building Service (PBS) Refrigerant Management and Reporting Standard Operating Procedure (SOP). This SOP reiterates and fine tunes EPA requirements and initiates some additional requirements applicable only to HFC refrigerants and appliances.

#### 5.7.2.1	Operations

The Contractor shall comply with EPA section 608 regulations (40 CFR Part 82 under section 608 of the Clean Air Act) and associated DC laws and regulations for refrigeration and air conditioning equipment. All HVAC mechanics performing repairs on refrigerated equipment shall possess a Universal Chlorofluorocarbon (CFC) Certification.

#### 5.7.2.2	Maintenance (Refrigerant Recycling, Reclamation, and Disposal)

The Contractor shall evacuate refrigerant to EPA-specified levels, using a certified recovery and/or recycling machine, prior to disposing of refrigeration and air conditioning equipment. The Contractor shall be responsible for refrigerators and refrigerant disposal in the FPB. When disposing of refrigerators and refrigerants, the Contractor shall give preference to reclamation to EPA-certified refrigerant reclaimers as a method of disposal. The Contractor shall notify the COR or designee and obtain approval prior to selling or offering for sale used refrigerators or refrigerant evacuated from DOL equipment.

#### 5.7.2.3	Testing/Inspections

The Contractor shall maintain and test emergency devices and systems, such as refrigerant monitors, automatic leak detection systems, alarms, and purge ventilation systems as part of the maintenance program. The Contractor shall use appropriate media to test sensors as well as alarm circuitry. The Contractor shall calculate and document the leak rate every time refrigerant is added to equipment, unless the addition qualifies as a seasonal variance.

#### 5.7.2.4	Reporting

The Contractor shall immediately report refrigerant leaks, at or above a 10% leak rate, to the COR or designee and take corrective action to repair leaks prior to the EPA 30-day deadline in compliance with section 608 of the Clean Air Act. Repair of leaks shall be documented by both an initial verification test and a follow-up verification test. In the event fines or penalties are levied by the EPA or an Air Quality Management District (AQMD), the Contractor may be charged the actual cost assessed. The Contractor shall submit reports to COR and EPA if systems containing 50 or more pounds of refrigerant leak 125% or more of their full charge in one rolling year.

### 5.7.3	Local Air Quality Management Operating Permits

The Contractor shall comply with the operating permit requirements of the Local AQMD and shall ensure operating permits for boilers; generators, and other emissions-producing equipment regulated by the local AQMD are up-to-date and have copies available to the COR or designee via the CMMS immediately upon request. In the event of fines or penalties levied by an AQMD, the Contractor shall be charged the cost as a performance deduction under the Adjusting Payments clause. The Contractor shall submit emissions reports when required by the regulating entity.

### 5.7.4	Stationary Engines

The Contractor shall comply with all applicable Federal and DC regulatory requirements for the notification of compliance, periodic inspection, monitoring, permitting, certification, registration, maintenance, personnel training, recordkeeping, and reporting for all regulated stationary engines. The Contractor shall ensure compliance with New Source Performance Standards (NSPS) for Stationary Compression Ignition Internal Combustion Engines, 40 CFR Part 60 Subpart IIII, NSPS for Stationary Spark Ignition Internal Combustion Engines, 40 CFR Part 60, Subpart JJJJ, and National Emission Standards for Hazardous Air Pollutants for Stationary Reciprocating, 40 CFR Part 63 Subpart ZZZZ.

### 5.7.5	Fuel Storage Tank Management

The Contractor shall comply with GSA Order PBS 1095.2A, Regulated Substances Storage Tank Management, and all applicable Federal and DC regulatory requirements for the periodic inspection, monitoring, permitting, certification, registration, maintenance, personnel training, and recordkeeping for underground and aboveground storage tanks. Where GSA policy and regulatory requirements differ regarding fuel storage tank management, the more stringent directive shall apply.

For non-regulated aboveground storage tanks (ASTs) and their systems, the Contractor shall implement best management practices regarding inspection, monitoring, and maintenance of the tanks and systems to prevent leaks, spills, and other releases.

### 5.7.6	Solid Waste

Non-hazardous solid waste and household recyclable material generated under this contract may be disposed in existing FPB containers at no charge to the contractor, except that the Contractor shall be responsible for the removal and proper disposal of all solid waste generated under this contract for any single project, work order, or repair that generates in excess of six cubic yards of solid waste, as determined by the COR or designee.

### 5.7.7	Polychlorinated Biphenyl (PCB) Control

The Contractor shall inspect all transformers containing PCBs and maintain records of such inspections in accordance with Federal and DC regulations. The COR or designee shall be notified immediately if any such equipment is found to contain PCBs or suspected to contain PCBs. Equipment verified to contain PCBs, except lighting ballasts, shall be labeled as containing PCBs. Any transformer leaks of PCBs shall be reported immediately to the COR or designee. The Contractor shall inspect all leaks in accordance with Federal and DC regulations. The Contractor shall properly dispose of caulk that contains PCBs. The Contractor shall take immediate action to contain all leaks.

### 5.7.8	Asbestos Management

The Contractor shall ensure that all employees, including replacement workers, receive asbestos training and refresher training in accordance with 40 CFR 763 and 29 CFR 1910. The Contractor shall follow all instructions for each asbestos class job as outlined in 29 CFR 1910. The training shall be conducted, at no additional expense to the Government, not later than 60 calendar days after the start date of the BPA. The Contractor shall submit written certification to the COR within five days of the completion of training.

The Contractor shall comply with applicable OSHA regulations and all applicable Federal and DC asbestos regulations. The Contractor shall immediately become familiar with, comply with, and recommend any appropriate changes to the Government’s FPB Asbestos Management Plan maintained the Office of Worker Safety, Health and Environment (OWSHE). If the Contractor disturbs material it suspects may contain asbestos, the Contractor shall immediately stop work and report the condition to the COR or designee.

### 5.7.9	Disposition of Hazardous Waste

The Contractor shall ensure that on-site hazardous waste management is compliant with all regulatory accumulation requirements (e.g., hold times, marking, labeling, container management). All Hazardous and Universal Waste shipping documentation shall be maintained for the life of the building. Universal Waste (e.g., fluorescent lamps, batteries, certain pesticides, used oil, mercury-containing equipment) in quantities subject to 40 CFR Part 273 shall be recycled or disposed of as Hazardous Waste. Preference is given to recycling intact items. Hazardous Wastes not subject to the Universal Waste Rule shall be managed in accordance with all applicable parts of 40 CFR Part 260. As co-generators, the Contractor and Government mutually agree that the Contractor shall perform generator duties on behalf of both parties. Generator requirements include hazardous waste generation, handling, accumulation, shipment, disposal, and also include exception reporting as required. The Contractor shall include the disposition of Hazardous and Universal Waste as a work order in the CMMS with documentation attached.

### 5.7.10	Backflow Prevention Devices

The Contractor shall maintain all existing backflow prevention devices and certify them as prescribed by applicable Federal and DC laws and regulations. Inspections shall be recorded in the CMMS and records provided to the COR or designee. A copy of the certification shall be posted at all backflow prevention devices. While the Government will generally pass on to the Contractor backflow testing notices received from local authorities, the Contractor is responsible for timely completion and submission of such test results regardless of receipt of such notices. In addition to other requirements, backflow prevention devices used on water-based fire suppression systems shall be inspected, tested, and maintained in accordance with NFPA 25, Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems.

### 5.7.11	Potable Water Systems

The Contractor shall comply with The Safe Drinking Water Act, PL 99-339, as amended, and the EPA Safe Drinking Water regulations, 40 CFR 141.43, Sections A and D. Potable water systems that are repaired, modified, serviced, or breached in any way shall be disinfected and flushed as needed prior to returning to service. The Contractor shall comply with all applicable Federal and DC laws and regulations, GSA Order PBS 1000.7A, Drinking Water Quality Management, and the PBS Desk Guide for Drinking Water Quality Management.

The Contractor shall perform potable water flushing and testing of the FPB drinking water points as identified by the COR and all the portable water points in the CDC on an annual basis. The Contractor shall deliver the results to the COR or designee. The samples shall be taken from fixtures (water fountains, sinks etc.) approved by the Government and tested, at a minimum, for levels of: Lead, Copper, Most Probable Number (MPN) Total Coliform, and Chlorine. All testing procedures and analysis shall be performed in accordance with the following, or more recent methods:

- EPA 600/4-79-020, Methods for Chemical Analysis of Water and Wastes.

- Standard Methods for the Examination of Water and Wastewater, 24th Edition.

- EPA Method 200.8, Determination of Trace Elements in Waters and Wastes by Inductively Coupled Plasma-Mass Spectrometry.

- GSA Order PBS 1000.7A, Drinking Water Quality Management.

### 5.7.12	Reporting

The Contractor shall provide all necessary information to comply with environmental reporting requirements and agency sustainability goals. The Contractor shall submit the following reports to the COR or designee annually:

Environmental Compliance. The Contractor shall collect and retain requisite data to produce and make mandatory reports required by environmental regulatory agencies including GSA programs, directives and orders, or as necessary to demonstrate ongoing compliance with environmental regulatory operational requirements. These reports include waste generation, shipment and disposal, hazardous materials storage (Tier II / Emergency Planning and Community Right-to-Know Act reporting), release reporting, fuel tank registration, operator training records, and notices of compliance for reciprocating internal combustion engines.

Sustainable Purchasing Practices. The Contractor shall submit information on sustainable purchasing practices specific to the performance of this Contract. Contractor shall provide records showing the monthly cost of sustainable cleaning products and materials purchased to the U.S. Department of Agriculture (USDA) and copies to the COR or designee as required by the Resource Conservation and Recovery Act (RCRA). The Contractor shall select from products that are EPA-designated (e.g. Comprehensive Procurement Guidelines (CPG)) and/or USDA-designated in the BioPreferred program and, all other factors (e.g., price, performance, availability) being equal, the Contractor shall select the CPG item. For other purchases, unless the Contractor receives an exemption from the COR or designee, the Contractor shall select products in the BioPreferred program over products with other sustainable attributes. More information is available at www.gsa.gov/buy-through-us/purchasing-programs/federal-strategic-sourcing-initiative/building-maintenance-operations/bmo-sustainabilityGuidance.

### 5.7.13	Contractor Pandemic Plan

The Contractor shall provide a Contractor Pandemic Plan, as required by the National Strategy for Pandemic Influenza. The Contractor shall prepare a plan to prevent and reduce the spread and mitigate the potential effects of an influenza pandemic on O&M. The Contractor shall submit the pandemic plan to the COR or their designee during the Phase-In period. During a declared pandemic the Government reserves the right to substitute disinfectant cleaners for non-disinfectant cleaners, when required by the Centers for Disease Control and Prevention.

The Contractor's pandemic plan shall include the following, at a minimum:

- Identify key Contractor personnel and their credentials for such an event

- Require and provide Contractor employees with appropriate training to fully address cleaning requirements during pandemic events

- Explain how Contractor staff will communicate with the Government

- Provide a contingency (backup personnel) to continue services if Contractor staff get sick and are unable to work

- Identify those procedures that will maximize air dilution, filtration, and sanitizing of HVAC air streams and implement those procedures as recommended by the Centers for Disease Control and Prevention

- Identify and develop procedures to monitor water use and levels of disinfectant and dissolved metals at the delivery point.

- Develop procedures to operate water systems to ensure delivered water contains residual disinfectant or adequate discharge temperature to prevent bacterial growth and adequate flow to limit the concentration of leaching metals to safe levels

- Identify those procedures that ensure timely, effective, and safe disinfectant cleaning practices

- Specify the type of PPE requirements for Contractor staff

- Provide protocols to ensure that the Contractor has sufficient supplies of filters, cleaners, PPE, and disinfectants

## 5.8	Energy and Water Efficiency

### 5.8.1	General

The Contractor shall operate equipment and systems per design as efficiently as possible without compromising service to the tenants.

### 5.8.2	Operations

The Contractor shall make full use of available analytic tools to diagnose problems and identify operational improvements. When equipment is being replaced, the Contractor, in coordination with the COR or designee, shall pursue the use of energy-efficient replacement parts and equipment items (e.g., Energy Star, FEMP-designated Energy Efficient products, Water Sense, Safer Choice) that shall meet or exceed the requirements of this PWS. Any rebates received from a service utility provider or Contractor shall be assigned to the Government.

### 5.8.3	Reporting

On a daily basis the Contractor shall read and record all available utility meters, advanced meters, and fuel meters (e.g., electric, gas, diesel fuel levels, water, cooling tower water makeup, irrigation) and include in the monthly report. The Contractor shall report monthly utility usage as compared to the previous year and to explain usage trends. The Contractor shall report all known or potential O&M impacts on ESPC/UESC equipment and/or ECMs.

## 5.9	Advanced Metering Systems

The Contractor shall verify daily that each advanced meter is functioning properly. The contractor shall operate, maintain, and repair, as necessary, all advanced meters.

## 5.10	Building Automation Systems (BAS)

### 5.10.1	Operations

The Contractor shall operate the BAS to maintain climate control in accordance with paragraph 5.1 and the established sequence of operations. Where these conditions cannot be maintained, the Contractor shall notify the COR or designee and develop and implement corrective action plans. Any adjustments to set points outside the parameters specified in paragraph 5.1 shall be approved in advance by the COR or designee.

The Contractor shall retain levels of expertise necessary to manage the BAS to meet the objectives of this Contract either by retaining a factory trained and certified technician on staff or by subcontracting with a qualified subcontractor. The Contractor shall have regular onsite expertise to perform basic daily operations and adjustments (e.g., setpoint adjustments, equipment start/stop to support Contractor or Government work, system optimization, troubleshooting, log review and analysis) and to operate the BAS during routine and manual / emergency operations.

The Contractor shall notify the COR or designee immediately if a sequence of operations, equipment, or schedule is not operating as designed or is resulting in unnecessary energy use. The Contractor shall document and track any manual overrides implemented in the BAS until the system is returned to automatic operation. The Contractor shall provide a report of all overrides in the monthly report.

The Contractor shall develop, update, and implement building recovery plans, in coordination with the Government, for loss of connectivity to the BAS to be able to operate the building systems manually.

The Contractor shall maintain the BAS hardware and software updated, cyber secured, and configured properly to enable it to remain connected to DOL network throughout the length of this contract, including any new regulations or requirements generated by OCIO.

The Contractor shall monitor the BAS for alarms at all times during normal duty hours and respond appropriately. The Contractor shall respond to BAS alarms outside normal duty hours that meet the definition of an Emergency in this PWS as an Emergency Callback work order and record it in the CMMS.

#### 5.10.1.1	DOL-Hosted System Requirements

All computers networked with building monitoring and control systems located inside FPB, or that provide storage of or access to DOL data, are required to be hosted exclusively on DOL’s physical network and system infrastructure, unless specifically approved by the COR or designee.

The Contractor shall:

- Ensure building monitoring and control systems, applications, and devices are implemented as designated in the GSA PBS P-100, Facilities Standards, the GSA PBS Building Technologies Technical Reference Guide, and Federal Information Security Modernization Act (FISMA) standards.

- Ensure that all internet protocol (IP) addressable devices, appliances, or software that communicates over the DOL network are assessed and have all identified vulnerabilities remediated in order to be approved by OCIO for use on the DOL network.

- Ensure that all devices that use wireless or radio frequency (RF)-based communications are approved by OCIO before use.

- Ensure that all building systems software (server and client) are hosted on Government furnished equipment (GFE) and approved by OCIO.

- Ensure that all IP traffic is managed by DOL and that IP addresses, routing, and switching equipment are government-furnished or approved by OCIO.

- Maintain and repair all cabled pathways connected to DOL’s network, including copper and fiber cabling, necessary to enable IP network communication among system devices and network components. Comply with GSA PBS P100, Facilities Standards, for all repairs or new installations.

- Comply with paragraph 1.6.8, Security Requirements. Identify any requirements for elevated access to the COR or designee for approval. If elevated access is approved, comply with all OCIO requirements.

- Ensure that no DOL-hosted building monitoring and control system is made accessible to the public internet or via any third-party network connection.

#### 5.10.1.2	Excepted Systems Requirements (not hosted on DOL’s system infrastructure)

The Contractor shall:

- Ensure the COR or designee approved antivirus software subscription is kept in effect and the software used is current at all times.

- Ensure all Contractor-provided software that has an End User License Agreement is presented to and approved by the COR or designee before that software is purchased.

- Ensure Contractor personnel do not use the BAS system to connect to websites.

- Ensure antivirus and spyware scans are conducted monthly.

- Be responsible for keeping all workstation and server operating systems updated. Critical updates shall be downloaded and installed at least monthly.

- Ensure complete data backup to a CD, DVD or flash drive, including trend logs and control software, is conducted whenever a software or programming change is made but no less frequently than monthly.

- Ensure disk drive maintenance, including defragmentation, is performed quarterly.

- Be responsible for software, licenses, and security updates to all Contractor-provided systems devices.

- Ensure a proper Configuration Management Plan is in place for the BAS devices and applications so the system can be supported.

- Ensure there is strong encryption on devices and applications for safeguarding sensitive data and login credentials.

- Ensure unnecessary services are disabled (e.g., FTP, Telnet) to protect the system from unnecessary access and a potential exposure point by a malicious attacker.

- Ensure unnecessary open ports are closed or blocked to secure against unprivileged access.

- Protect against Cross-Site Scripting, which is a common vulnerability in web applications where an attacker can compromise or take control of a site.

- Enforce Least Privilege, where proper permissions are enforced on a device or application so that a malicious attacker cannot gain access to all data.

- Protect against Insufficient User Access Auditing, when device or application does not have a mechanism to log/track activity by user.

- Notify the COR or designee of any end-of-life systems and application/system software that is no longer supported by the manufacturer.

- Use the latest supported and approved operating systems.

- Ensure that all proposed standard installation, operation, maintenance, updates, and patching of software do not alter the configuration settings from the approved U. S. Government Configuration Baseline (USGCB).

- Ensure that the use of commercially provisioned circuits to manage building systems is strictly prohibited. All circuits shall be provisioned through OCIO.

- Ensure workstations and servers running building monitoring and control systems are not connected to the public internet.

- Adhere to all OCIO directives and regulations.

- Provide a network diagram of all IP-addressable devices that terminate on the DOL network to the COR or designee. Include OCIO in the design phase of the network infrastructure.

### 5.10.2	Maintenance

The Contractor shall maintain the BAS as designed. The Contractor shall perform maintenance required to ensure that all BAS devices function properly and repair or replace components that fail. The Contractor shall implement required BAS software and firmware updates and security patches.

The Contractor shall coordinate BAS vendor activities necessary to facilitate any upgrades the Government deems necessary for the functionality and/or security of the BAS over and above those necessary for standard system operations. The Government may upgrade or change control system software or reprogram control systems during the performance period of the Contract. If the Government provides operator level training and operator level documentation for the Contractor’s use, the Contractor shall not claim additional payment for services relating to the new or upgraded control software or systems programs.

The Contractor shall not modify sequences of operation, control programs, or run systems manually without concurrence of the COR or their designee. Where a sequence of operation change is approved, the Contractor shall provide accurate edits to the Sequence of Operation to document the changes made.

## 5.11	Fire Protection and Life Safety Equipment and Systems

### 5.11.1	General

The Contractor shall:

- Utilize the latest edition of the applicable NFPA code or standard.

- Ensure all fire protection and life safety systems, equipment, and markings are kept operational at all times, except while being tested or repaired.

- In the event fire protection and life safety equipment is not returned to operational condition, notify the COR or designee and provide a fire watch at no additional charge to the government.

- Ensure all maintenance and pre-planned impairments of the fire protection or life safety systems and equipment have been approved by the COR or designee prior to the Contractor performing any work.

- Comply with all appropriate safety code requirements. If the Contractor encounters equipment that is in a condition that shall endanger life or property, the Contractor shall immediately notify the COR or designee of the condition requiring immediate action. Within 24 hours following the notification of the COR, the Contractor shall provide to the COR or designee a written report of the hazardous condition and recommended corrective action.

- Create a work order in the CMMS for any deficiency identified by the Contractor during a required inspection. Provide evidence of correcting such deficiency, unless funding is not available, with the subsequent Contractor’s Monthly Progress Report after correction action is completed.

- Provide all tools, supplies, and equipment necessary to inspect, test, and maintain the fire protection and life safety equipment and systems in accordance with applicable NFPA codes or standards.

### 5.11.2	Fire Alarm System Services and Emergency Communication Systems

The Contractor shall ensure compliance with NFPA 72, National Fire Alarm and Signaling Code, in the performance, inspection, testing, acceptance, and preventive maintenance or repair of fire alarm and notification systems, equipment and components of said systems and all other ancillary devices that operate related equipment. The Contractor shall maintain Remote Supervising Station monitoring service equipment, all fire alarm transmitters, and related equipment.

Fire alarm system or emergency communications system inspection, testing, maintenance, and repair shall be performed during normal working hours when it does not interfere with building or tenant operations. Testing that activates notification devices, initiates elevator recalls, activates HVAC shutdown, or interferes with building or tenant operations will be conducted outside normal working hours, requires COR approval, and will be conducted without additional costs to the Government. The Contractor shall schedule with the COR or designee all testing and non-emergency shutdowns of such systems and ensure that back-up protection is provided by the Contractor (e.g., arrangement of additional personnel stationed in the areas affected and at the fire alarm system control unit or emergency communications control unit) any time such system is temporarily out of service.

When impairments to systems occur or when impairments are identified during inspection, testing, or maintenance activities, the Contractor shall inform the COR or designee immediately. The Contractor shall follow the impairment procedures outlined in NFPA 72 and provide a fire watch in areas left unprotected at no additional cost to the Government. The fire watch shall remain in place until the systems are completely restored.

The Contractor shall be liable, without additional cost to the Government, for all local fees associated with unwanted fire alarm system activations that are caused by the Contractor and require local jurisdiction fire department response.

The Contractor will report unwanted fire alarms to the COR or designee at the close of each business day and provide the following information: the time, date, and location of the system activation; a brief description of the fire alarm system activation; device activated; a brief reason for why the fire alarm system activated (if known); and how the fire department was notified and what time they arrived on scene.

The Contractor shall provide a daily report to Government before 9am each day identifying all fire alarm system troubles, supervisory alarms, and alarms.

### 5.11.3	Water-Based Fire Protection Systems

The Contractor shall ensure compliance with NFPA 25 in the inspection, testing, maintenance and repair of water-based fire protection systems, and in the performance; inspection, testing, preventive maintenance, and repair of all devices that are components of water-based fire suppression systems.

Water-based fire protection system inspection, testing, preventive maintenance, and repair shall be performed during normal duty hours when the work does not interfere with building operations. When such inspection, testing, preventive maintenance, or repair is expected to interfere with building operations, the work shall be performed outside normal duty hours without additional cost to the Government. The Contractor shall schedule with the COR or designee all non-emergency shutdowns of the water-based fire protection system and back-up protection shall be provided by the Contractor any time the water-based fire protection system is expected to be out of service for more than ten hours. When a water-based fire protection system is returned to service, the Contractor shall verify that the system is working properly in accordance with the component action requirements in NFPA 25.

When impairments to the system occur or when impairments are identified during inspection, testing, or preventive maintenance activities, the Contractor shall inform the COR or designee immediately. The Contractor shall follow the impairment procedures outlined in NFPA 25 and provide a fire watch in areas left unprotected or if the system is out of service for more than ten hours in a 24-hour period without additional cost to the Government. The fire watch shall remain in place until the water-based fire protection system is completely restored to service. Temporarily shutting down a system as part of performing the routine inspection, testing, preventive maintenance, or repair on that system while under constant attendance by qualified personnel and where the system can be restored to service shall not be considered impairment.

### 5.11.4	Fire-rated Door Assemblies

Reserved.

### 5.11.5	Fire Damper and Combination Fire/Smoke Dampers

The Contractor shall ensure compliance with the NFPA 80, Standard for Fire Doors and Other Opening Protectives, in the inspection, testing, maintenance, and repair of all fire dampers, radiation dampers, and combination fire / smoke dampers. Maintenance of combination fire / smoke dampers shall also meet the requirements contained in NFPA 105, Standard for Smoke Door Assemblies and Other Opening Protectives.

### 5.11.6	Smoke Doors Assemblies

Reserved.

### 5.11.7	Smoke Dampers

The Contractor shall ensure compliance with NFPA 105, Standard for Smoke Door Assemblies and Other Opening Protectives, in the inspection, testing, preventive maintenance, and repairs of all smoke dampers.

### 5.11.8	Portable Fire Extinguishers

The Contractor shall provide all tools and supplies necessary to properly perform inspection, testing, maintenance, and replacement of portable fire extinguishers at the end of service life, in accordance with NFPA 10, Standard for Portable Fire Extinguishers, including appendices, as well as applicable OSHA standards. Anywhere NFPA 10 states "should," it shall be taken to mean “shall." The Contractor is responsible for meeting the inspection, maintenance, testing frequencies, testing methods, and documentation requirements outlined in NFPA 10.

GSA PBS P100, Facilities Standards for the Public Buildings Service, paragraph 7.9.5 provides guidance on locations that do not require portable fire extinguishers. Before inspecting, testing, repairing, or replacing a portable fire extinguisher, the Contractor shall determine if it is still required in accordance with the P100. The Contractor shall notify the COR or designee of their findings and recommendations. The COR or designee shall then provide the Contractor with guidance on whether the work shall continue or the portable fire extinguisher shall be permanently removed (including restoring the former mounting location) and disposed, in either case at no additional cost to Government.

### 5.11.9	Non-Water-Based Fire Extinguishing Systems

The Contractor shall provide all tools and supplies necessary to properly perform inspection, testing, maintenance, and replacement of non-water-based fire extinguishing systems at the end of service life. This includes fire extinguishing systems servicing the FPB cafeteria, CDC, and the DOL Secretary’s kitchen. The Contractor shall ensure compliance with the following specified codes in the inspection, testing, preventive maintenance, and repairs of the following types of non-water-based fire extinguishing systems:

- Carbon dioxide extinguishing systems: NFPA 12, Standard on Carbon Dioxide Extinguishing Systems.

- Halogenated extinguishing systems: NFPA 12A, Standard on Halon 1301 Fire Extinguishing Systems.

- Dry chemical extinguishing systems: NFPA 17, Standard for Dry Chemical Extinguishing Systems.

- Wet chemical extinguishing systems: NFPA 17A, Standard for Wet Chemical Extinguishing Systems.

- Commercial kitchen fire extinguishing systems: NFPA 96, Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations.

- Clean agent fire extinguishing systems: NFPA 2001, Standard for Clean Agent Fire Extinguishing Systems.

### 5.11.10	Smoke Control Systems

The Contractor shall ensure compliance with NFPA 92, Standard for Smoke Control Systems, in the inspection, testing, preventive maintenance, and repairs of smoke control systems.

### 5.11.11	Emergency and Standby Power Systems

The Contractor shall ensure compliance with the following specified codes in the inspection, testing, preventive maintenance, repairs, and exercising of equipment per the manufacturer’s recommendations for the following types of emergency and standby power systems:

- Emergency power supply systems: NFPA 110, Standard for Emergency and Standby Power Systems.

- Stored electrical energy emergency and standby power systems: NFPA 111, Standard on Stored Electrical Energy Emergency and Standby Power Systems.

### 5.11.12	Emergency Lighting Systems and Exit Signage

The Contractor shall ensure compliance with NFPA 101, Life Safety Code, in the inspection, testing, preventive maintenance, installing, relocating, and repair of emergency lighting systems, emergency lighting equipment, and exit egress marking systems.

### 5.11.13	Fire Resistance Rated Construction

The Contractor shall ensure compliance with the International Fire Code (IFC) and NFPA 221, Standard for High Challenge Fire Walls, Fire Walls, and Fire Barrier Walls, in the inspection, preventive maintenance, repair, or installation of new systems and assemblies used for structural fire resistance, fire resistance rated construction, separation of adjacent spaces, and construction installed to resist the passage of smoke to safeguard against the spread of fire and smoke within a building or the spread of fire to or from buildings. All materials and fire-stop systems provided or maintained under this Contract shall comply with these codes.

Materials and fire-stop systems used to protect membrane and through penetrations along with joints and voids in fire resistance rated construction and construction installed to resist the passage of smoke shall be maintained. The materials and fire-stop systems shall be securely attached to or bonded to the construction being penetrated with no openings visible through or into the cavity of the construction. Where the system design number is known, the system shall be inspected to the listing criteria and manufacturer’s installation instructions.

The Contractor shall notify the COR or designee of areas in the building that firestop systems are lacking or compromised.

### 5.11.14	Lightning Protection Systems

The Contractor shall develop and implement an inspection and maintenance plan that requires the same inspections and maintenance as recommended in NFPA 780, Standard for the Installation of Lightning Protection Systems.

### 5.11.15	Chemical Sensors

Reserved.

## 5.12	Tours

### 5.12.1	General

The Contractor shall tour major building systems, equipment, tanks and anything requiring tours mandated by any acts, codes, or regulations as contained in this PWS or any Federal or DC requirements. To accomplish this objective the Contractor shall develop a Tour Plan and submit it to the COR or designee for approval no later than the end of the Phase-In period. A tour shall be a combination of physical visits and reviewing automated systems. Tours are an opportunity to view equipment in different phases of operation, make adjustments, validate controls, verify set points, record performance, check efficiency, assess physical condition of mechanical space, and evaluate overall safety. The Contractor shall develop tours at frequencies and using methodologies that are of value to operations, inclusive of analytical decision making intended to optimize operations based on real time performance data.

### 5.12.2	Proactive Facility Tours

The Contractor shall conduct periodic tours of the building to proactively identify and remedy any issues pertaining to lighting, bathroom fixtures, and other tenant environmental comfort concerns. The tours shall work in conjunction with the Contractor’s energy conservation efforts, proactive work orders, and equipment condition assessments, to identify and solve issues before they impact building or tenant operations. All findings noted during the tours shall be tracked through work orders in the CMMS.

### 5.12.3	Minimum Tour Frequencies

- Daily: Major HVAC equipment (when in operation), including steam system, steam converters, chillers, major pumps and valves, cooling towers, pneumatic control air compressors, and air handler rooms; medium voltage switchgear, transformers, and electrical equipment rooms; fire alarm system and control panels; and special HVAC and uninterruptible power systems (UPS) for critical functions.

- Weekly: Distributed HVAC equipment including package units, external condensers, pumps, and motors; sewage ejectors; fire pumps; condensate drip pans; and generators. Incorporate moisture control tours to prevent building damage, minimize mold contamination, illuminate leaks, and reduce health risks related to moisture.

- Biweekly: Battery systems.

- Monthly: Low voltage switchgear, panelboards, transformers, and electrical equipment rooms.

### 5.12.4	Monitoring of Central Plant Equipment

Reserved.

### 5.12.5	Operating Logs and Tour Check Sheets

Contractor shall maintain operating logs and tour check sheets for major equipment. Documentation shall be completed at the time of tours. Information recorded in the logs shall be sufficient to track the operating hours and performance history of the equipment. Records shall be kept of tours and action items needed based upon tour discovery. Operating logs and tour check sheets shall be a part of the tour plan, and a tour check sheet shall be established for any space identified as requiring a tour. The Contractor shall upon request make the operating logs and tour check sheets available for inspection by the COR or designee. A tour check sheet shall contain at a minimum:

- General space condition with any discrepancies annotated.

- Broken/inoperable equipment identified with work order status.

- Accurate listing of equipment inspected during tour.

- Equipment operating data.

- Equipment status with regard to operational parameters.

Contractor shall evaluate discrepancies in operating logs and tour check sheets, and the operational performance shall be investigated and repaired when necessary.

The Contractor shall submit to the COR or designee the proposed operating logs and tour check sheets during the Phase-In period.

### 5.12.6	Reporting

The Contractor shall immediately report to the COR or designee any problems or conditions that may potentially impact the efficient operation of the building or create a negative impact on a tenant.

## 5.13	Repairs

### 5.13.1	General

A “repair” is an act of restoring inoperable, dysfunctional, or deteriorated equipment, systems, or material to a fully functional, non-deteriorated state. Repairs involve some combination of labor and repair or replacement of equipment, parts, components. or materials. The Contractor shall create a work order in the CMMS for all identified repairs.

The Shared Liability Amount for this contract is $5,000.

The Contractor shall perform reimbursable and non-reimbursable repairs as defined in this PWS. Repairs are handled on a shared liability basis. This contract has a shared liability amount threshold which means the Contractor is responsible for the first $5,000 of the repair cost for each repair.

The intent of this contract is to ensure that most repairs are accomplished by inhouse onsite Contractor personnel. However, the Government recognizes that occasionally there are certain specialized repairs that require specialized skills outside the skill sets of the Contractor personnel.

If the Contractor identifies a repair that it believes is of such a specialized nature that a specialized subcontractor is required to complete the repair properly, the Contractor shall provide written justification in advance to the COR or designee for approval of the need to use a subcontractor. If approved, the cost of the subcontractor’s labor, material, and equipment rental shall be treated as a repair part for the purpose of calculating the repair cost.

Other than the agreed upon Contractor percentage markup identified at award of this BPA per paragraph 5.15.2.4, no other cost (e.g., Contractor project manager hours, Contractor supervisor hours, Contractor overhead or profit, additional Contractor fees) shall be added to the subcontractor’s cost. No Contractor markup shall ever be added to Contractor labor costs (including overtime or outside normal duty hours labor) or material or equipment rental executed directly the Contractor.

Shared liability shall not apply when repairs are required as a result of Contractor or subcontractor negligence. In such instances, the Contractor shall be responsible for all costs associated with the repair.

All replacement parts installed under this contract shall be from the original manufacturer matching the existing part, unless unavailable, and of comparable or higher quality and efficiency. Materials and parts that are visible to building occupants shall be to building standard and maintain the same appearance as similar materials and parts in the occupied space. Components of control systems shall be replaced so as to maintain the tie-in to the control system with no degradation of data throughput, memory, point capacity, data acquisition, or programmability. Motors shall be replaced with premium efficiency motors as defined by the National Electrical Manufacturers Association (NEMA) MG 1 standard or in compliance with local utility demand-side management guidelines. Transformers shall be replaced with new transformers meeting the NEMA TP-1 standard. Replacement of variable frequency drives shall be done in accordance with NEMA Application Guide for AC Adjustable Speed Drive Systems. Energy Star-rated equipment shall be installed where available and when there is no engineering or operational reason not to select an Energy Star product. Energy-consuming items shall be the most efficient in their class.

The Contractor shall stock commonly used items and stay in good standing with a network of suppliers that shall deliver ordered items without delay. Repairs delayed due to supply houses refusing to do business with the Contractor for any reason, is not an excuse to delay the repair. Any equipment components / systems that can no longer be repaired shall be replaced. These replacements shall be considered a repair, and the shared liability amount threshold shall apply.

Contractor shall submit manufacturer’s cutsheets, catalog data, specifications, or other acceptable documentation to the COR or designee for all parts or material provided by the Contractor or a subcontractor prior to ordering.

### 5.13.2	Repair Types

#### 5.13.2.1	Non-Reimbursable Repair

A non-reimbursable repair is a repair or replacement requiring no more than $5,000 in cost for repair parts, materials, and equipment rental only (including any approved subcontracting costs). The cost of consumable parts and materials shall not be calculated as part of the Contractor’s repair parts and material costs. Non-reimbursable repairs are entirely the Contractor’s responsibility with no reimbursement from the Government. Non-reimbursable repairs shall be completed in accordance with the work order timelines in paragraph 5.14.

#### 5.13.2.2	Partially Reimbursable Repairs

Partially Reimbursable Repairs shall be identified as a single incident, not an accumulation of various repairs (bundling). If the cost for a repair exceeds $5,000 and has been approved by the COR or designee, it becomes a reimbursable repair. A partially reimbursable repair is reimbursable to the Contractor for the portion of the cost exceeding the $5,000 repair threshold (Government portion of shared liability). The COR or designee shall determine if the repair can be made during normal duty hours. If the Contractor uses in-house labor during normal duty hours to perform the repair, no labor shall be included in the total cost of the repair when determining the shared liability amount. If the COR or designee approves the work to be performed outside normal duty hours using Contractor inhouse labor, the labor rate shall be the overtime rate established in the Contract and the labor cost shall be included in the total cost of the repair when determining the shared liability amount. If the COR or designee approves the work to be subcontracted, the cost proposal shall include the subcontractor’s labor hours by trade, hourly rate by trade, parts and materials listing with associated costs itemized, equipment rental costs, and subcontractor overhead and profit.

The completion date of reimbursable repairs shall be mutually agreed upon by the COR or designee and the Contractor in writing.

Example:

A repair is identified and estimated by the Contractor to cost $7,200 for repair parts, materials, and equipment rental only. The Contractor identifies that inhouse employees can complete the repair on normal duty hours. The COR or designee will verify and approve the need for the repair, the $7,200 estimated cost, and the acceptability of the Contractor performing the repair during normal duty hours. In this example, the Contractor shall pay the first $5,000 of the repair and the Government will pay the remaining $2,200.

#### 5.13.2.3	Fully Reimbursable Repairs

Repairs that are caused by third-party vandalism or misuse/abuse by third parties (including civil disturbance and bombings) are fully reimbursable. Acts of God are only fully reimbursable if the total cost of damage caused by a single act (e.g., a single hurricane, tornado, earthquake, hail, flood, snowstorm) exceeds the Shared Liability Amount, excluding inhouse normal duty time labor, and the Contractor took all reasonable precautions to prepare ahead of the storm. A single Act of God causing damage less the Shared Liability Amount, excluding inhouse normal duty time labor, shall be a non-reimbursable repair.

### 5.13.3	Warranties

The Contractor shall contact installers or manufacturers, as appropriate, for work that is covered under a warranty and maintain records of warranty service. The Contractor shall ensure current-in-force warranty information is maintained in CMMS and checked prior to maintenance on affected equipment. The Contractor shall avoid actions that would invalidate a warranty, unless authorized by the COR or designee. If an installer or manufacturer fails to comply with the terms of a warranty, the Contractor shall immediately notify the COR or designee. Contractor shall organize, retain, and fille all warranty information. Warranty information shall be available for inspection by the government and shall be turned over to the government at the end of the contract.

### 5.13.4	Third-Party Contractors

The Government reserves the right to order repairs from a third-party contractor. If the repair is a reimbursable repair, the Government shall inform the Contractor of the outside source’s price, and deduct $5,000, or the third-party contactor’s price, whichever is less, from the Contractor’s payments.

## 5.14	Work Orders

### 5.14.1	General

The Contractor shall provide adequate staff to respond to work orders during normal duty hours.

The Contractor shall utilize the Government-provided CMMS, ServiceNow, to manage, track, and report on all work under this contract. The Contractor shall perform only as an end user in the CMMS. All system programming is the responsibility of the Government. The Contractor shall assist the Government with the continued refinement of the application, functionalities, and processes.

The Contractor shall maintain service desk operations during the normal duty hours of 6:00am – 6:00pm, Monday-Friday, except Holidays per paragraph 1.6.4, receiving work orders by walk-in visit, phone, email, radio, automated submission by the BAS or other system, or online through the ServiceNow portal.

The Contractor shall serve as the responsible main point of contact for all work relating to engineering and facilities and shall also accept all work orders, regardless of if the request is for work included in the scope of this contract or not. The Contractor shall route work orders that are not under this contract (e.g., custodial, pest control, mis-routed IT support, landscaping) to the appropriate department for action. The Contractor shall exclude any work orders for work not in the scope of this contract from all reports (e.g., work order completion times) created in the CMMS.

The Contractor shall enter all data into the CMMS necessary to manage work order execution as directed by the COR or designee, but at minimum, including point of contact information, location, problem description, pictures, problem cause, remedy, timestamps, work start, work completion, labor hours, material cost, equipment rental cost, and all status update communication with the customer or Government. The Contractor shall update work orders in ServiceNow timely, preferably within one hour of change in status, but in all cases on the same duty day as the work status changed.

The Contractor shall use the CMMS mobile work management tools and Government-furnished tablets to the greatest extent practicable.

The Contractor shall provide reports from the CMMS as directed by the COR or designee. The Contractor’s performance shall be assessed by tracking the completion record, performance against requirements, tenant satisfaction, and the overall accountability and organization of the work under this contract. The Government shall use the data collected by the Contractor to monitor and analyze the building and O&M activities. The Government shall use the data in the CMMS to evaluate the Contractor under the Quality Assurance Surveillance Plan (QASP).

### 5.14.2	Emergency Work Orders

Emergency work orders are work during normal duty hours to correct failures that constitute an immediate danger to personnel or property, including broken water pipes, stalled elevators with trapped passengers, electrical power outages, electrical problems that may cause fire or shock, gas or oil leaks, major air conditioning or heating problems, or any work considered by the COR or designee to be of an emergency nature. The Contractor shall respond to an emergency work order immediately. The Contractor shall remain on the job until the emergency situation has been secured and adequate temporary repairs have been made. Permanent repairs shall be carried out in accordance with this PWS. Emergency work orders are also referred to as “Critical” priority or “Priority 1” work orders in the CMMS.

### 5.14.3	Emergency Callback (Outside Normal Duty Hours)

Emergency callback work orders are work outside normal duty hours to correct failures that constitute an immediate danger to personnel or property, including broken water pipes, stalled elevators with trapped passengers, electrical power outages, electrical problems that may cause fire or shock, gas or oil leaks, major air conditioning or heating problems, or any work considered by the COR or designee to be of an emergency nature. The Contractor shall respond to emergency callback work orders immediately 24/7/365 (i.e., within the shortest possible time consistent with the mechanic's location) but not more than two hours from the time of first notification. The Contractor shall remain on the job until the emergency situation has been secured and adequate temporary repairs have been made. Permanent repairs shall be carried out in accordance with this PWS. The Contractor shall provide a written account of any emergency callback; including costs incurred and plan for permanent correction of the problem, to the COR or designee no later than the morning of the next business day. If the emergency callback is expected to take more than two hours to resolve, the Contractor shall contact the COR or designee for approval. Emergency callback work orders are also referred to as “Critical” priority or “Priority 1” work orders in the CMMS.

### 5.14.4	Urgent Work Orders

Urgent work orders are work to correct failures that interrupt or otherwise adversely impact building or tenant operations. Examples include inoperative electrical circuits, extreme temperature complaints (over 80 degrees or under 64 degrees), inoperative lighting above a workstation, flush valve stuck open, equipment malfunctions impacting a tenant’s operations, or any work considered by the COR or designee to be of an urgent nature. The Contractor shall respond to urgent work orders within one hour during normal duty hours. The Contractor shall remain on the job until the urgent repairs have been made. Permanent repairs shall be carried out in accordance with this PWS. Urgent work orders are also referred to as “High” priority or “Priority 2” work orders in the CMMS.

### 5.14.5	Routine Work Orders

Routine work orders are work to correct deficiencies that do not interrupt or otherwise adversely impact building or tenant operations. The Contractor shall respond promptly to routine work orders and complete the required work within five business days of notification. The Contractor shall immediately notify the COR or designee with a written extension request when the routine work order cannot be completed within the specified timeframe. Routine work orders are also referred to as “Moderate” priority or “Priority 3” work orders in the CMMS.

### 5.14.6	Low Priority Work Orders

Low priority work orders are work that corrects a non-critical deficiency not visible to building occupants or provides a desired enhancement that is not critical to building or tenant operations. The Contractor shall complete low priority work orders within ten business days of notification or notify the COR or designee when the work order cannot be completed in this timeframe. Low priority work orders are also referred to as “Priority 4” work orders in the CMMS.

### 5.14.7	CMMS Management

The Contractor shall:

- Keep all records and databases current and accessible by the Government.

Keep all CMMS data through the length of the contract and ensure it is available to the Government at the end of the contract.

Correct any data errors or bring to the attention of the COR or designee any errors that cannot be corrected.

Update CMMS database frequently, including all certifications, inspection records, and third-party reports.

Ensure all work orders include labor hours, costs, and closeout notes.

Manage in-progress work orders and report to the Government any barriers that can potentially impact successful and timely completion.

Provide weekly and monthly work order status reports, meet contract submittal requirements, and generate any other reports from the CMMS data as directed by the COR or designee.

Respond to Government requests for information from the CMMS within one business day.

Use the CMMS to track all equipment, assets, work orders, preventive maintenance, inspections, testing, quality control, and other associated information necessary for efficient O&M.

Maintain accurate equipment data in CMMS including, at a minimum, equipment ID, equipment type, equipment description, manufacturer, model number, serial number, equipment status, and location. Audit the CMMS inventory on an ongoing basis and update equipment records as needed to maintain accuracy.

In order to maintain a complete facility record, enter data, reports, or work orders on behalf of third-party contractors executing facility work in the FPB.

Utilize and support existing and future labeling and labeling conventions.

Establish and maintain an asset identification system for new and replacement equipment compliant with CMMS-readable asset identification coding.

Complete the initial upload of equipment data into ServiceNow during the Phase-In period. The government will provide the initial equipment inventory from the existing emaint system that is being deprecated. Contractor is responsible for validating and correcting Government-provided inventory before uploading it to ServiceNow.

## 5.15	Additional Services Work Request (ASWR)

### 5.15.1	General

The COR shall order additional services at their discretion. Additional services shall include any services related to operations, maintenance, repairs, construction, systems upgrade, system operation, or tenant facility services within the general scope of the contract but not already a requirement of the contract. Examples: Installation of new equipment that either raises or lowers the level of effort required by the Contractor; Tenant-funded enhancement work such as large area painting or carpeting or installation of new walls, doors, or window coverings.

### 5.15.2	Price Proposal

The Government shall issue the Contractor an ASWR for additional work within the general scope of this Contract. The Contractor shall provide a proposal within five business days of receipt of the ASWR. The proposal shall include a brief description of the technical approach to completing the ASWR and detailed pricing on a firm-fixed price basis. At a minimum, the price to complete the ASWR shall include parts and materials, equipment rental, labor (categories, hours, and rates), subcontracting, and indirect costs as described below.

#### 5.15.2.1	Parts, Materials, and Equipment Rental

The price for any parts, materials, or equipment rental required to complete the ASWR shall include a description of the estimating methodology used by the Contractor to determine the reasonableness of the proposed price (e.g., review of manufacturer catalogs, review of competitive quotes, or justification of only one available source).

#### 5.15.2.2	Labor

The price for labor required to complete the ASWR shall identify the labor categories, labor hours per labor category, and labor rates from the price schedule in this BPA and the contractor’s GSA 03FAC Facilities Maintenance and Management Schedule.

#### 5.15.2.3	Subcontracts

The Contractor shall identify the price of any subcontract necessary to complete the ASWR and the Contractor’s methodology to determine that the level of effort and price of the subcontract is reasonable (e.g., competitive quotes for the work, independent estimate using industry standards, information to assist the Government in determining the reasonableness of the proposed subcontract). The Contractor shall compete subcontractor opportunities for the work to the maximum extent practicable and provide written justification to the COR or designee if the subcontract opportunity cannot be competed. Subcontractor agreements shall be submitted to the Government with the Contractor’s proposal and shall include, at a minimum, labor (categories, hours, and rates), parts, materials, equipment rental, overhead, and profit. All services performed by a subcontractor shall be in accordance with the contractor’s GSA 03FAC Facilities Maintenance and Management Schedule labor rates and BPA pricing.

#### 5.15.2.4	Indirect Costs (Markup)

The Contract shall submit, with their proposal, a proposed percentage markup for subcontracted repair and ASWR work. This markup shall be applied only to subcontractor costs to cover the Contractor’s additional effort required to award, supervise, manage, quality assure, and warranty subcontractor work, including Contractor’s overhead, profit, and any other reasonable and customary costs. The actual percentage markup shall be made part of this Contract, and all subsequently awarded task orders, at contract award. Other than the agreed upon Contractor percentage markup identified at award of this BPA, no other cost (e.g., Contractor project manager hours, Contractor supervisor hours, Contractor overhead or profit, additional Contractor fees) shall be added to the Contractor or subcontractor’s cost.

### 5.15.3	Proposal Review

The Government shall review the Contractor’s ASWR proposal and may request additional information regarding the technical approach or the price of the prospective ASWR.

### 5.15.4	Ordering and Invoicing

If the Government (in its sole and absolute discretion) is satisfied with the technical approach and the price of the ASWR, the COR or designee may order the ASWR, in writing, if priced at less than $2,500. The Contractor shall accept the Government Purchase Card (GPC) as a method of payment.

If the ASWR is priced at $2,500 or greater, the CO may order the ASWR by a separate task order on this BPA using the Contractor’s submitted proposal.

### 5.15.5	Cost Documentation

The Contractor shall provide all paid invoices for all materials, parts, equipment rental, and subcontractor costs (including certified payrolls and a Release of Claims) not later than 30 calendar days after completion of the ASWR work.

Documentation for work ordered on the GPC shall be provided at the time payment is processed.

### 5.15.6	Schedules

The Contractor shall provide a project schedule for all ASWR work within 10 calendar days of award. Schedule shall include a well-defined work breakdown structure, specific activity definitions, logical dependencies, assigned resources, and estimated durations for all tasks. Schedule shall include start/end dates, key milestones, and a critical path to monitor progress, ensuring tasks are manageable and realistic. In no case will a single task duration exceed two weeks; any task longer than two weeks shall be divided into multiple tasks with their own start/end dates. Contractor shall provide an updated schedule to the COR or designee weekly throughout the length of the ASWR work until completion. When providing updates, the Contractor shall, in writing, specifically identify all changes to the schedule, provide comprehensive explanations for any changes, and identify impacts to the operation of the FPB due to schedule changes.

## 5.16	Building Management and Support Services

### 5.16.1	Support to Third-Party Contractor Work

Projects for the major repair or enhancement of the FPB are often initiated by DOL or GSA and awarded to third-party contractors. Generally, these projects are lengthy and complicated in nature, affecting several major building systems during the course of construction. To deliver successful project results and minimize impact on building tenants and daily operations, high levels of coordination are necessary.

To assist the Government in these efforts, and when requested by the COR or designee through a CMMS work order, the Contractor shall provide reasonable and competent assistance during normal duty hours to Government personnel and third-party contractors, at no additional cost to the Government, during project planning, design, and construction. Examples include reviewing design documents and supporting energy studies and ESPC/UESC contracts, commissioning services, engineering studies, building condition evaluations, renovation project design and construction, and equipment or system surveys. Such assistance shall include escorting personnel through spaces in the building, explaining the operation and condition of equipment and systems, locating utility feeds, securing utilities and equipment, and providing access to trend data, maintenance records, reference library materials, and other pertinent building technical data. The COR or designee will inform the Contractor as far in advance as possible of the actual date and time these services are needed. The Contractor shall identify any impact on regular scheduled work to the COR or designee.

### 5.16.2	Miscellaneous Work

Numerous small projects/requirements are generated monthly by building occupants. Accomplishing these requirements generally requires skilled labor, common supplies, and small tools of the building trades. At no additional cost to the Government, the Contractor shall provide up to 100 hours of inhouse labor per calendar month and up to $2,500 of material or equipment rental per calendar month when requested by the COR through a CMMS work order to accomplish discretionary work not otherwise included in this contract. The labor hours and material / equipment rental limits are not cumulative (i.e., if the Government does not order its entire allotment in a month, the labor hours and material / equipment rental limit for that month expires and does not rollover to the next month). The Contractor shall utilize the CMMS to track this work and shall keep the Government regularly informed on their expenditure against the monthly limits. The Contractor shall immediately cease work and inform the COR or designee if they determine any work order will cause the Contractor to exceed a monthly limit under this paragraph.

### 5.16.3	Inspection Services

During construction and upon completion of a space renovation project executed by the Government utilizing a third-party contractor, the Contractor shall inspect the area to ensure the work does not negatively impact on the operations and maintenance of the building. The Contractor shall, for example, verify that the third-party contractor appropriately zoned and labeled HVAC supply and return ductwork, appropriately labeled all installed equipment, appropriately adjusted all HVAC and lighting controls, correctly labeled all panelboards and outlets, and correctly keyed all doors to the Contractor-managed key system. Inspection services will be requested by the Government on a CMMS work order.

### 5.16.4	Flags

The Contractor shall maintain all flag poles and any flag supporting equipment (e.g., ropes, snap links, pulleys, operating mechanism) needed to raise and lower the flags.

The Contractor shall raise and lower the large (approx. 30’ x 50’) flags mounted on the Constitution Ave face and 3rd St face of the building, when directed by the Government on a CMMS work order. The Contractor shall properly store the large flags when not in use. The Contractor shall maintain and replace, as necessary, all mounting hardware for the flags. The Contractor shall regularly inspect the flags for wear or damage and notify the COR or designee of flag conditions. The Contractor shall install, remove, store, and maintain all flag lighting.

### 5.16.5	Overtime Utilities (OTU)

The Contractor shall, at the direction of the COR through a CMMS work order, provide OTU to tenant agencies. The Contractor shall operate equipment by hand or through the BAS, as required. The Contractor does not have to be physically present but shall ensure that the utilities are scheduled and operate as requested. The Contractor shall document OTU requests in the monthly report.

## 5.17	Monthly Report

Not later than the fifth business day of each calendar month, the Contractor shall provide a monthly report to the Government detailing operations and maintenance as of the last day of the prior calendar month. The monthly report shall include:

- CMMS output showing status of all work orders.

Performance in accordance with the CMMS Service Level Agreements (SLAs).

A report of all work completed per the predictive and preventive maintenance plan and an explanation, including corrective action plan, for all issues identified or work not completed as scheduled.

Explanation of any equipment operating in manual mode or any other overrides to sequences of operations, including the Contractor’s plan to return the equipment to automatic mode.

Operating schedule changes.

Description of any lost time accidents or other safety problems, including incidents involving hazardous materials.

Hazardous waste reports.

Copies of quality control inspections performed.

Building management support services provided, including support to third-party contractor work, miscellaneous work, and inspection services.

Water treatment test results.

Reports from any testing performed under this contract.

Refrigerant control logs.

Fuel levels and purchase.

Emergency generator and transfer switch operating status and test results.

Inspections, reports, and test results on all fire protection and life safety equipment and systems required by this contract.

Meter readings and utility usage trends, including analysis of any anomalies and recommendations.

Any O&M reports required by ESPC or UESC contracts.

Any other reports identified in this PWS.

Any other data the Contracrtor determines would be helpful to the Government to understand the operations and maintenance of the FPB.

Any other reports determined by the COR or designee.

## 5.18	Reference Library

The Contractor shall create, maintain, and update a comprehensive reference library that includes building design and record documents, renovation and equipment retrofit design and record documents, maintenance reference documents, applicable codes and standards, fire protection system as-built drawings, fire protection system operations and maintenance manuals, HVAC system operations and maintenance manuals, building operating plan, energy and other building technical studies, hazardous materials surveys, and other documents necessary to document the design, function, and condition of the building as necessary to operate and maintain the building and its systems. The Contractor shall safeguard this information and maintain it in a secure and organized manner on the bookshelves in the foyer of room N0066.

# Part 6

# Maintenance Specific Requirements

## 6.1	Predictive and Preventive Maintenance Plan

The Contractor shall establish an effective predictive and preventive maintenance plan for scheduling and performing maintenance on all building equipment and systems requiring scheduled maintenance under the scope of this Contract. The Contractor shall submit an outline plan as part of the Contractor’s proposal and shall submit a completed plan not later than the end of the Phase-In period for approval by the COR or designee. The plan shall include the Contractor’s approach to maintenance, a list of equipment / systems receiving scheduled maintenance, the procedure / tasks to be performed, and the frequency. The plan shall, at a minimum, incorporate the procedures / tasks identified in the 2025 PM Guide Cards at Technical Exhibit 4. Not less than 10 business days after Government approval of the plan, the Contractor shall incorporate it into the BOP and CMMS.

The 2025 PM Guide Cards are generic in nature and not intended to substitute for manufacturer's instructions or applicable codes, standards, or industry best practices. The Contractor shall incorporate applicable procedures / tasks from manufacturer's instructions and applicable codes, standards, and industry best practices when developing the scheduled maintenance program in the CMMS. The Contractor shall ensure the scheduled maintenance program includes all procedures / tasks necessary to maintain the manufacturer’s warranty on the equipment / system.

At a minimum, the Contractor shall include the following equipment in the plan:

- Equipment normally requiring periodic replacement of consumable components.

Equipment normally requiring periodic or occasional cleaning.

Equipment with moving parts.

Equipment that is prone to failure before overall obsolescence of the system it serves.

Equipment in American National Standards Institute (ANSI) / InterNational Electrical Testing Association (NETA) Maintenance Testing Specifications for Electrical Power Equipment.

Equipment requiring inspection, testing, or maintenance in accordance with NFPA codes and standards.

Equipment requiring maintenance in accordance with any other provision of this Contract.

The Contractor shall complete scheduled maintenance per the approved plan in the month scheduled in the CMMS and document the work in the CMMS.

## 6.2	Reserved

## 6.3	Air Distribution Equipment

### 6.3.1	General

The Contractor shall operate and maintain air distribution systems to provide acceptable indoor air quality for building occupants. Air distribution systems include all types of air handling equipment, package units, rooftop units, fan coil units, direct expansion units, dry coolers, and similar equipment providing space conditioning. The contractor shall operate and maintain all computer room air conditioning (CRAC) / Liebert units and similar units, whether operational or not, whether they condition an active computer room or not.

### 6.3.2	Operation

The Contractor shall operate air distribution systems in accordance with their design, the approved sequence of operations, American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE) standards and guidance, and any other requirements of this Contract. The Contractor shall adjust systems, including controls and the BAS, per the BOP and in response to work orders. The Contractor shall monitor system operation, identify system alarms and anomalies, and respond accordingly restore proper system operation. The Contractor shall protect systems from freezing.

### 6.3.3	Maintenance

The Contractor shall execute the COR-approved predictive and preventive maintenance plan. The plan shall include, at a minimum: applying lubricants; sealing filter racks against bypass air flow; cleaning fan housings, fans, coils, dampers, air diffusers, grilles, air handling unit (AHU) sections, and equipment rooms; and replacing consumable parts and components, including filters. The contractor shall respond to demand work orders from building occupants in order to restore proper system operation.

### 6.3.4	Air Filters

The Contractor shall record filter minimum efficiency reporting value (MERV) ratings in the CMMS during the Phase-in period and maintain MERV ratings during maintenance and filter changing. The Contractor shall use only high-efficiency air filters with a known MERV rating per ANSI/ASHRAE Standard 52.2. The Contractor shall use the highest possible MERV rating without significantly reducing design air flow. The Contractor shall submit proposed filters for approval by the COR or designee before installation.

At a minimum, for an AHU with pre- and post-filters, the Contractor shall replace the pre-filters and single layer filters as deemed necessary by the differential pressure (DP) gauges or BAS-connected monitoring devices, and no less than quarterly. Post or main filters will be changed when deemed necessary by the DP gauges or BAS connected monitoring devices, and no less than annually. Where DP is utilized to determine filter change periodicity, the Contractor shall change filters at the DP provided by the equipment manufacturer. The Contractor shall calibrate DP gauges annually. The Contractor shall change filters for rooftop units, variable air volume boxes, fan coil units, CRACs, and other air distribution filters in a like manner to AHUs just described above and per manufacturer recommendations. The Contractor shall maintain minimum ventilation standards per ASHRAE Standard 62.1.

### 6.3.5	Testing and Inspecting

The Contractor shall conduct regular inspections of air distribution equipment. The Contractor shall inspect condensate drip pans for proper operation not less than quarterly. The Contractor shall treat condensate drip pans, as necessary, to control the growth of algae, mold, and other organisms.

## 6.4	Chiller Systems

### 6.4.1	Operation

The Contractor shall operate the chiller systems in accordance with established operational standards, manufacturer’s guides, industry standards, or as otherwise directed by the COR or designee, in order to provide acceptable indoor air quality for building occupants. The Contractor shall maintain daily chiller operation logs.

### 6.4.2	Maintenance

The Contractor shall execute the COR-approved predictive and preventive maintenance plan. Maintenance shall be accomplished by the chiller manufacturer’s authorized service technician.

### 6.4.3	Testing/Inspecting

The Contractor shall conduct nondestructive chiller tube analysis (eddy current testing) on all chillers every three years. The test shall be performed by a Level II technician certified in accordance with the American Society for Nondestructive Testing (ASNT) SNT-TC-1A, Personnel Qualification and Certification in Nondestructive Testing. The test shall be performed in accordance with current ASME standards. The Contractor shall take pictures of the tubes, tube sheets, and end plates immediately after the removal of the end plates prior to brushing the tubes and again after the brushing of the tubes. The Contractor shall upload the pictures to the CMMS. The Contractor shall notify the COR or designee at least two business days prior to the removal of the end plates so that the Government can observe the condition of the tubes right after the removal of the end plates. The Contractor shall provide the written nondestructive chiller tube analysis report, including findings and recommendations, to the COR or designee within 14 calendar days after the test. The Contractor shall establish and execute a chiller oil analysis program per manufacturer’s recommendations.

## 6.5	Cooling Towers

### 6.5.1	Operations

The Contractor shall operate the cooling towers in accordance with established operational standards, manufacturer’s guides, industry standards, or as otherwise directed by the COR or designee, in order to provide acceptable indoor air quality for building occupants. The Contractor shall operate the cooling towers efficiently and shall propose to the COR or designee for approval any operational improvements that would improve efficiency.

### 6.5.2	Maintenance

The Contractor shall execute the COR-approved predictive and preventive maintenance plan. The Contractor shall properly maintain cooling towers by inhibiting and removing mineral scale, corrosion, bacterial contamination, and general fouling of the water, and by physically cleaning the tower on a regular basis.

### 6.5.3	Testing

The Contractor shall test the cooling tower water in accordance with the water treatment section of this contract.

## 6.6	HVAC Water Management

### 6.6.1	HVAC Water Management Plan

The Contractor shall prepare and submit to the COR or designee for approval during the Phase-In period a comprehensive HVAC water management plan that includes operating, cleaning, maintaining, corrosion monitoring, seasonal equipment layups, water treatment for both open and close loops, and reporting on all related actions and analysis. The plan shall provide the COR or designee a quality assurance guide by which to assess the operating, maintaining, testing, and reporting of all activities associated with the HVAC water systems. The Contractor shall ensure compliance with GSA Order PBS 1000.7A, Drinking Water Quality Management, and the PBS Desk Guide for Drinking Water Quality Management. The Contractor shall provide all equipment, chemicals, and services (including application) required to control corrosion, scale, algae, and bacterial growth in all HVAC equipment and systems throughout the building. All equipment installed for water treatment and corrosion monitoring shall be conveyed to the Government at the end of the contract.

### 6.6.2	Operation

The Contractor shall execute HVAC water management in accordance with the COR-approved HVAC water management plan to ensure optimum system performance and provide acceptable indoor air quality for building occupants.

The Contractor shall operate the steam system in the building to ensure optimum system performance and provide acceptable indoor air quality for building occupants. The Contractor shall open / close valves and bleed / fill the steam system as necessary to support GSA steam plant operations and maintenance.

The Contractor shall comply with all applicable local sanitation requirements and discharge regulations.

### 6.6.3	Maintenance

The Contractor shall execute the COR-approved predictive and preventive maintenance plan. The Contractor shall implement an effective HVAC water loop maintenance program to ensure optimum system performance and provide acceptable indoor air quality for building occupants. The Contractor shall correct any issues identified during testing or operation.

### 6.6.4	Testing and Inspecting

The Contractor shall establish water treatment and testing frequencies that give an accurate and regular indication of whether the maintenance performed is adequately keeping the HVAC system water within the limits established in the HVAC water management plan. Testing frequencies shall be established based on manufacturer’s recommendations with input from the COR or designee.

The Contractor shall perform a comprehensive initial water treatment analysis (laboratory analysis) during the Phase-in period to assist in developing the HVAC water management plan and to establish a baseline to validate the effectiveness of the Contractor’s water management. The Contactor shall report results of the analysis to the COR or designee immediately upon receipt. The Contractor shall correct all non-compliant conditions in accordance with the Repairs section of this PWS. Once the parameters are within the established tolerances, the Contractor shall be responsible for maintaining equipment and chemistry at no additional cost to the Government.

The Contractor shall engage a qualified independent water treatment specialist to draw water samples per the water management plan. Upload results to the CMMS. Immediately notify the COR or designee of any results outside the established parameters and implement corrective actions. Retest water after completion of corrective actions to verify the issue was corrected.

The Contractor shall test all glycol-water solutions in the building monthly to determine the percentage glycol and annually for pH, reserve alkalinity, inhibitor levels, and degree of contamination. The Contractor shall add any glycol or additives required to establish and maintain proper chemistry and system operation. The Contractor shall notify the COR or designee if tests determine full replacement is necessary. Full replacement will be executed under the Fully Reimbursable Repairs section of this PWS, if the Government (at its sole discretion) decides to execute the work.

### 6.6.5	Reporting

The Contractor shall report results of periodic water treatment and testing per the water management plan in the monthly report. Monthly reports shall include, at a minimum:

- Testing dates, procedures, and results.

- Make up water quantities, when metered.

- Chemical amounts and types added to the systems.

- Glycol-water system test results.

- Tolerance and range criteria set forth in the plan compared to actual testing results.

- Remediation actions taken during the month.

- A 12-month running trends for all results.

- Any other data needed to provide a comprehensive profile of the systems.

### 6.6.6	Open Loop Water Management Criteria Reporting

| Test | Test Frequency | Operating Range |
| --- | --- | --- |
| Tower Water Conductivity | Weekly | 160-2400 mmhos (110-1600 ppm) |
| Makeup Water Conductivity (Hardness) | Weekly | 40-600 mmhos (30-400 ppm) |
| pH | Weekly | 7.5-9.5 |
| Corrosion Monitoring (Coupon Test) | Quarterly | Iron: 2-5 mils / year Copper: 0.2-0.5 mils / year |
| Bacteria | Quarterly Any time system has been shut down for 7 consecutive days | <1000 cfu / ml |
| Chlorides | Weekly | <250 ppm as Cl <410 ppm as NaCl |
| Sulfites | Weekly | 50-100 ppm SO3 80-160 ppm Na2SO3 |
| Corrosion Inhibitor Residual | Weekly | As defined by water treatment consultant |
| Oxidizing Biocide Residual | Weekly | As defined by water treatment consultant |
| Legionella pneumophila | Any time total bacteria >1000 cfu / ml Repeat treatment and testing until total bacteria <1000 cfu / ml and L. pneumophila <10 cfu / ml | <10 CFU / ml |

### 6.6.7	Closed Loop Water Management Criteria Reporting

| Test | Test Frequency | Operating Range |
| --- | --- | --- |
| pH | Monthly | 7.5-9.5 |
| Total Dissolved Solids or Conductivity | Quarterly | <2000 ppm or <2500 µS / cm |
| Polyphosphates (PO4) | Monthly | 10-20 ppm |
| Sulfites | Monthly | 50-100 ppm SO3 80-160 ppm Na2SO3 |
| Bacteria | Monthly | <1000 cfu / ml |
| Corrosion Monitoring (Coupon Test) | Semiannually | Iron: <0.5 mils / year Copper: <0.2 mils / year |
| Corrosion Inhibitor Residual | Monthly | As defined by water treatment consultant |
| Legionella pneumophila | Any time total bacteria >1000 cfu / ml Repeat treatment and testing until total bacteria <1000 cfu / ml and L. pneumophila <10 cfu / ml | <10 CFU / ml |

### 6.6.8	Chemical-Free Water Treatment System

HVAC loops that are treated by chemical-free water treatment systems shall be tested and maintained by an authorized Original Equipment Manufacturer (OEM) certified vendor. The Contractor shall provide a qualified independent water treatment specialist to draw a set of water samples monthly. Tests shall be performed as described in the water management plan. Samples shall be analyzed and a report containing all results shall be submitted to the COR or designee with the monthly report.

## 6.7	Domestic Plumbing Systems

The Contractor shall operate, maintain, and repair all domestic plumbing systems inside and outside the FPB to the site property line or point of demarcation with the utility provider. Systems include, but are not limited to, drinking fountains and filters, drinking water chillers, restrooms, kitchens, locker rooms and showers, water heaters, stormwater structures / stormwater best management practices, backflow preventers, and decorative fountains. The Contractor shall ensure all system drains, including storm drains, windowsill drains, fan coil unit drains, kitchen exhaust hood drains, planter box drains, and roof drains, remain clear and unobstructed. The Contractor shall take all necessary steps to prevent odors emitting from drains or other plumbing systems into occupied space, including maintaining water in traps. The Contractor shall clear toilet and sink blockages. The Contractor shall ensure compliance GSA Order PBS 1000.7A, Drinking Water Quality Management, and the PBS Desk Guide for Drinking Water Quality Management.

## 6.8	Lighting Systems

The Contractor shall establish and maintain adequate lighting levels throughout the facility interior and exterior to allow tenants to be productive, feel secure, and egress in case of emergencies. The Contractor shall operate and maintain lighting in areas including entrances, landings, steps, stairwells, sidewalks, parking areas, garages, arcades, highly decorative courtrooms, auditoriums, and other areas within the building or site. The Contractor shall operate and maintain historic fixtures, fountain lights, security lights, flag lights, building-mounted fixtures, pole lighting, elevator car interior lighting, modular and stand-alone furniture lighting, ground lighting located adjacent to the facility and extending to the property line, and other lighting within the building or site.

Replacement lamps shall be LED, regardless of existing lamp type, and be the most efficient products available, unless otherwise approved by COR or designee. Replacement lamps shall match existing lamp lumen output and color rendering index, unless otherwise approved by COR or designee. Contractor shall not install incandescent, fluorescent, or high intensity discharge lamps without approval of the COR or designee.

The Contractor shall establish and implement a recycling program for fluorescent lamps and other light bulbs in accordance with EPA and GSA standards.

The Contractor shall properly manage and dispose of hazardous waste.

## 6.9	Electrical Equipment

Contractor shall perform all preventive maintenance, testing, and inspections of electrical distribution equipment, cabling, switchgear, panel boards, circuit breakers, switches, automatic transfer switches, relays, network protectors, transformers, control systems, and all associated equipment for both low voltage (<600V) and high voltage (5kV class and 15kV class) equipment. The Contractor shall comply with NFPA 70B, Standard for Electrical Equipment Maintenance, and NETA guidelines for the inspection, testing, and maintenance of electrical equipment. When such testing, maintenance, or repair interferes with building operations, it shall be performed outside normal duty hours without additional cost to the Government.

The Contractor shall coordinate all utility shut down scheduling with the electrical utility company. The Contractor shall be responsible for all costs associated with the utility shutdown, switching, grounding, and lockout/tagout with no additional cost to the Government. The Contractor shall coordinate power shutdowns with the building COR or designee. The Contractor shall submit a schedule and shut down plan at least 30 calendar days in advance to the COR or designee for approval. The Contractor shall execute outages on order from the utility or COR, including opening, closing, racking out and racking in high voltage (>600V) circuit breakers, and grounding switchgear or cables as directed at no additional cost to the government, except that the government will fund labor outside duty hours per the Emergency Callback section of this PWS.

The Contractor shall maintain the existing master clock system, including adjusting for daylight savings time. The Contractor shall install, maintain, and replace common area clocks, whether standalone or on the master clock system, including replacing batteries.

## 6.10	Emergency Power Equipment

### 6.10.1	General

The Contractor shall ensure that all standby and emergency power equipment and related systems are ready to respond at all times to protect the occupants of the building and to maintain critical services during the event of a normal power outage. These services include performance, inspection, testing, acceptance, and preventive maintenance and repair of standby and emergency power equipment, load banks, supplies, electricity distribution from the generators, and fuel distribution to the generators.

### 6.10.2	Operation

All Fuel tanks shall be filled by the Government or the previous contractor at the beginning of the contract period and by the Contractor at the end of this contract period. The Contractor shall check and record all diesel tank levels monthly and record in the CMMS.

The Contractor is responsible for any consumables used during day-to-day operation of a generator, including exercising the generator and related electrical components, testing of oil and fuel reserves, and fuel tank filling. The Contractor shall be reimbursed for the cost of the fuel for fuel consumed by the operation of a generator for an extended period (more than four hours per event) or due to a power loss. If the operation of the generator is caused by Contractor negligence, the Contractor shall be liable for the full cost of refueling. The Contractor shall not allow the fuel level to drop below 70 percent. When the fuel level drops to 70 percent, the Contractor shall immediately notify the COR or designee of the need for refueling and the cost associated and receive approval from the COR or designee prior to refilling the tank. The Contractor shall provide fuel up to $3,500 per contract year at no additional cost to the Government. The Contractor shall maintain a running log containing the amount of fuel used and the log shall be available to the COR or designee upon request. The Government will pay for all fuel after the $3,500 annual fuel cost limit is reached.

### 6.10.3	Maintenance

The Contractor shall execute the COR-approved predictive and preventive maintenance plan in accordance with manufacturer’s recommendations, NFPA 110, Standard for Emergency and Standby Power Systems, and NFPA 111, Standard on Stored Electrical Energy Emergency and Standby Power Systems.

### 6.10.4	Testing and Inspecting

The Contractor shall conduct monthly testing of the generators and transfer switching with a licensed and certified provider. The Contractor shall provide any required load bank at no cost to the government.

Generator oil shall be tested by a qualified person at least annually and analysis and recommendations shall be provided to COR or designee. Testing shall be performed per ASTM D6595, Standard Test Method for Determination of Wear Metals and Contaminants in Used Lubricating Oils or Used Hydraulic Fluids by Rotating Disc Electrode Atomic Emission Spectrometry, and ASTM D445, Standard Test Method for Kinematic Viscosity of Transparent and Opaque Liquids (and Calculation of Dynamic Viscosity), and recorded in the CMMS. Contractor shall take corrective actions and follow any recommendations provided by the testing facility. Oil changing shall only be performed based on testing and analysis recommendations from a UL approved laboratory. The Contractor shall change oil filters per manufacturer's recommendation or industry standards.

The Contractor shall have fuel oil tested by a qualified third-party subcontractor at minimum annually. The analysis and recommendations shall be provided to COR. The Contractor shall take corrective action, follow recommendations provided in the analysis, and document the work in the CMMS. The Contractor shall condition and treat fuel oil to establish and maintain the minimum quality standards established in American Society for Testing and Materials (ASTM) D396-08a, Standard Specification for Fuel Oil.

Glycol-water solutions shall be tested annually to determine the percentage glycol, pH, reserve alkalinity, inhibitor levels, and degree of contamination. The Contractor shall complete required corrective action based on test results. The Contractor shall maintain minimum freeze protection and inhibitor levels.

## 6.11	Reserved

## 6.12	Vertical Transportation Systems

The Contractor shall test, operate and maintain vertical transportation systems in accordance with ASME A17.1, Safety Code for Elevators and Escalators, ASME A17.2, Guide for Inspection of Elevators, ASME A17.4, Emergency Personnel Guide for Elevators, ASME A17.6, Standard for Elevator Suspension, Compensation, and Governor Systems, and A17.7, Performance-Based Safety Code for Elevators and Escalators.

The Contractor shall maintain fire protection equipment and systems, and ventilation and exhaust systems within hoist ways, elevator lobbies, and elevator machine rooms. The Contractor shall maintain elevator cab lighting, fixtures, ballasts, and lamps installed in elevator cars and within the ceilings of cars, electrical equipment (including elevator transformers and disconnects) not directly part of elevator systems, and HVAC systems associated with elevator machine rooms and systems.

## 6.13	Architectural and Structural Systems

### 6.13.1	General

Exterior components of this work include precast concrete systems, foundations, minor exterior wall components, retaining walls, docks, levelers, sidewalks and drives. Interior components of this work include walls, floors, doors, ceiling systems, soundproofing, insulation, directories, flooring, specialty finishes, and lighting.

The Contractor shall perform all architectural and structural maintenance and repairs or replacements to the building interior and exterior extending to the property line. The Contractor shall ensure the integrity of elements and materials in compliance with Federal and DC laws and regulations and national codes and standards. The Contractor shall ensure the building is free of missing components or defects that could affect the safety, appearance, or intended use of the facility or could prevent any electrical, mechanical, fire protection, life safety, plumbing, or structural system from functioning in accordance with its design intent.

Architectural maintenance, repairs, and replacements are intended to maintain the integrity of the building envelope (e.g., preventing water leaks through proactively addressing cracks, minor tuckpointing failures, reattaching loose roof flashing, fixing windows cracked by weather or seal failures) and address safety hazards.

All proposed replacement items shall be consistent with design documents and match existing equipment in quality, dimension, material, quality of workmanship, finish, and color.

### 6.13.2	Painting

Painting under this contract is only to touch-up specific damaged areas. Painting shall extend to logical break points such as the floor, ceiling, corners, or door frames to avoid a patched look.

Repainting to correct for normal wear and tear to painted surfaces over time (cyclic paint) is not required. Restriping of parking areas, driveways, roads, and vehicle inspection areas is required where striping is damaged or worn in a specific location, but not for general wear and tear of a large area over time.

### 6.13.3	Mechanical Rooms

The mechanical rooms, including walls and the equipment located within the mechanical rooms, shall be painted to maintain the professional appearance of the room and equipment, and as needed for OSHA compliance. The Contractor shall comply with A13.1, Scheme for the Identification of Piping Systems. Existing painted floors shall be maintained, and bare floors shall be sealed. The Contractor shall not disturb materials suspected to contain lead-based paint. Rooms with excessive noise shall be labeled "Hearing Protection Required" and appropriate PPE shall be placed outside the room entrances. Mechanical rooms shall be maintained free of trash, debris, material, tools, and loose equipment. Spare parts or tools may be kept in an organized manner in a mechanical room only if they are specifically required by the operating machinery in the room. All mechanical spaces shall be kept locked at all times and all locks shall be maintained in a serviceable condition.

### 6.13.4	Historic Buildings

Although the FPB has been determined to be ineligible for listing on the National Register of Historic Places, it will still be treated as if it is eligible with respect to work affecting exterior building appearance or public spaces inside the building. The Contractor shall get approval from the COR if any work on the building may impact the building appearance.

### 6.13.5	Signage

The Contractor shall install, maintain, repair, update, and replace signage throughout the FPB, both common building signage and tenant-specific office signage. Signage shall match existing or be as directed by the COR or designee. The Contractor shall install, maintain, repair, and replace poster frames located in each elevator and bulletin boards throughout the FPB. The Contractor shall maintain directories, including electronic directories, but not electronic directories belonging to an individual tenant.

### 6.13.6	Roofs

The Contractor shall execute routine preventive maintenance and repairs to the roofs as necessary to maintain the integrity of the building envelope and protect the building from damage. The Contractor shall make minor repairs (e.g., ceiling tiles replacement, installing rain umbrellas) caused by the current deteriorated condition of the roof.

### 6.13.7	Roof Anchorages

The Contractor shall provide for annual third-party inspections and a ten-year recertification of designated roof anchorage points by qualified personnel. Roof anchorages (davits) shall be inspected in accordance with the anchor manufacturer’s requirements and any additional requirements contained in the installation certification. If equipment or support areas are identified or suspected of failure, the anchorage and its points of support shall be immediately tagged “out of service” and reported to the COR or designee. The Contractor shall comply with 29 CFR 1910.27. Inspection reports shall be provided to the COR or designee.

## 6.14	Physical Access Control Systems

The Contractor shall maintain physical access control systems including bollards, gates, garage doors, and related equipment. At the direction of the COR or designee, the Contractor shall remove and reinstall bollards to support Government requirements at no additional cost to the Government.

## 6.15	Child Development Center (CDC)

The Contractor shall maintain all exhaust hood systems, kitchen equipment, laundry equipment, fire suppression systems, wooden cabinets, doors, pinch guards, playground gates, playground equipment, playground outdoor carpet covering, fencing, carbon monoxide detectors, and fixed equipment associated with the CDC. The Contractor shall support the annual shutdown by identifying and executing all required maintenance work. The Contractor shall complete all work identified in the Annual Child Care Center Survey.

# Part 7

# Administrative Instructions

## 7.1	Initial Deficiency Inspection / Initial Deficiency Report

During the Phase-In period, the outgoing and incoming contractors and the COR or designee shall make a complete and systematic initial inspection of building equipment and systems for which operations, maintenance, and repairs are covered by this PWS. This inspection shall be primarily only a visual inspection. The purpose of this inspection is to discover and list, with pictures, all deficiencies that exist in the equipment and systems covered by this PWS, as well as the incoming Contractor's price for correcting each deficiency, to document in the Initial Deficiency Report. This report shall cover all equipment and systems within the building, regardless of whether or not they are listed in the building inventory. The incoming Contractor shall submit the Initial Deficiency Report to the COR or designee within 30 calendar days of contract award, including cost estimates valid for 120 days from date of report submission.

The Government may (at its sole discretion) elect to have all, some, or none of this work performed by the outgoing contractor, incoming Contractor, Government employees, or third-party contractors.

Deficiencies discovered after the submission of the Initial Deficiency Report shall not be considered pre-existing for purposes of this contract, unless equipment is operational and could not be secured and inspected. Any piece of equipment or system that could not be inspected shall be identified as such within the CMMS. An estimate of when the Contractor reasonably expects to be able to inspect the piece of equipment shall be provided.

Equipment that can be brought into an acceptable level of operation through basic preventive maintenance and operational procedures shall be made operational at no additional cost to the Government and shall not be documented in the Initial Deficiency Report.

Any dispute between the Government and the Contractor as to the classification of an Initial Deficiency Report items shall be resolved under FAR 52.233-1, Disputes. When an existing deficiency in an item is corrected, the Contractor shall assume full responsibility for the subsequent repair of the item as covered under the terms of this contract at no additional cost to the Government. Nothing in the Initial Deficiency Report shall be construed as diminishing the obligations imposed by this contract upon the Contractor to operate any deficient item (to the extent operable) or to adjust or maintain any such item.

# Part 8

# Publications

The following publications and laws are incorporated by reference as setting quality, performance, and design standards for work required in this PWS. Unless a specific date is provided, references are for the current edition published at the time of issue of the solicitation, including any addenda or errata published by the issuing organization. The Contractor is responsible for obtaining access to all referenced documents at its own expense.

- 29 CFR part 1910, OSHA General Industry Standards

- 29 CFR part 1926, Safety and Health Regulations for Construction

- 40 CFR, Protection of Environment

- 41 CFR Subchapter C, Real Property

- ASHRAE Standard 230, Commissioning Process for Existing Buildings and Systems

- ASHRAE Guideline 4, Preparation of Operating and Maintenance Documentation for HVAC&R Systems

- ASHRAE Standard 15, Safety Standard for Refrigeration Systems

- ASHRAE Standard 34, Designation and Safety Classification of Refrigerants

- ASHRAE Standard 55, Thermal Environmental Conditions for Human Occupancy

- ASHRAE Standard 62, Ventilation for Acceptable Indoor Air Quality

- ASHRAE Standard 100, Energy and Emissions Building Performance Standard for Existing Buildings

- ASHRAE Standard 111, Testing, Adjusting, and Balancing of Building HVAC Systems

- ASHRAE Standard 188, Legionellosis: Risk Management for Building Water Systems

- ASME A17.1 Safety Code for Elevators and Escalators

- ASME A17.2, Guide for Inspection of Elevators, Escalators, and Moving Walks

- ASME Boiler and Pressure Vessel Code

- ASME CSD-1, Control and Safety Devices of Automatically Fired Boilers

- ASSE A1264.2, Provision of Slip Resistance on Walking/Working Surfaces

- Child Care Center Design Guide PBS-140

- Clean Air Act, 42 USC 7401 et seq.

- Clean Water Act, 33 USC 1251 et seq.

- DOE/EE-0157, International Performance Measurement and Verification Protocol

- Energy Policy Act of 2005, 42 USC 13201 et seq. and 42 USC 15801 et seq.

- Energy Independence and Security Act of 2007, 42 USC et seq.

- EPA Green Book

- EPA Purple Book

- GSA Building Technologies Technical Reference Guide

- GSA Facilities Standards for the Public Buildings Service

- GSA PBS P100, Facilities Standards for the Public Buildings Service

- GSA Order PBS 1000.7A, Drinking Water Quality Management

- GSA Order PBS 1000.1B, Asbestos Management

- GSA Order PBS 1095.2A, Regulated Substances Storage Tank Management

- GSA PBS Property Managers Child Care Desk Guide

- GSA PBS Refrigerant Management and Reporting Standard Operating Procedure

- GSA PM Guide Cards

- GSA Technology Policy for PBS-Owned Building Monitoring and Control (BMC) Systems

- International Building Code

- International Fire Code

- International Plumbing Code

- International Mechanical Code

- IWCA I-14.1, Window Cleaning Safety Standard

- National Board of Boiler and Pressure Vessel Inspectors, National Board Inspection Code

- NEMA TP-1, Guide for determining energy efficiency for distribution transformers

- NEMA MG-1, Motors and Generators

- NEMA Application Guide for AC Adjustable Speed Drive Systems

- NETA Maintenance Testing Specification for Electrical Power Distribution Equipment and Systems

- NFPA 10, Standard for Portable Fire Extinguishers

- NFPA 12, Standard on Carbon Dioxide Extinguishing Systems

- NFPA 12A, Standard on Halon 1301 Fire Extinguishing Systems

- NFPA 13, Standard for the Installation of Sprinkler Systems

- NFPA 14, Standard for the Installation of Standpipe and Hose Systems

- NFPA 17, Standard for Dry Chemical Extinguishing Systems

- NFPA 17A, Standard for Wet Chemical Extinguishing Systems

- NFPA 20, Standard for the Installation of Stationary Pumps for Fire Protection

- NFPA 25, Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems

- NFPA 54, National Fuel Gas Code

- NFPA 70, National Electrical Code

- NFPA 70B, Standard for Electrical Equipment Maintenance

- NFPA 70E, Standard for Electrical Safety in the Workplace

- NFPA 72, National Fire Alarm and Signaling Code

- NFPA 80, Standard for Fire Doors and Other Opening Protectives

- NFPA 85, Boiler and Combustible Systems Hazards Code

- NFPA 92, Standard for Smoke Control Systems

- NFPA 96, Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations

- NFPA 101, Life Safety Code

- NFPA 105, Standard for Smoke Door Assemblies and Other Opening Protectives

- NFPA 110, Standard for Emergency and Standby Power Systems

- NFPA 111, Standard on Stored Electrical Energy Emergency and Standby Power Systems

- NFPA 780, Standard for the Installation of Lightning Protection Systems

- NFPA 2001, Standard on Clean Agent Fire Extinguishing Systems

- NICET publications and issuances

- National Institute for Safety and Health publications and issuances

- Resource Conservation and Recovery Act, 42 USC 6901 et seq.

- Safe Drinking Water Act, PL 93-523, as amended, 42 USC 300f et seq.

- Sheet Metal and Air Conditioning Contractors National Association HVAC Systems Testing, Adjusting and Balancing

- Toxic Substances Control Act, 15 USC 2601- 2629 et seq.

# Part 9

# Technical Exhibit Index

Technical Exhibit 1 – Performance Requirements Summary

Technical Exhibit 2 – Deliverables Schedule

Technical Exhibit 3 – Building Information Sheet

Technical Exhibit 4 – 2025 PM Guide Cards

Technical Exhibit 5 – Building Operating Plan (BOP) Template

# Technical Exhibit 1

# Performance Requirements Summary

| Performance Objective | Standard | Allowable Percentage Deviation from Standard | Method of Surveillance |
| --- | --- | --- | --- |
| Training Para. 1.6.15 | All required training is completed within the specified time requirements | 5 | 100% by the COR |
| Phase-In Period Para 1.6.21 | All required services are performed within the specified time requirements | 5 | 100% by the COR |
| Equipment Inventory Para. 5.4 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Workplace Safety and Health Program Para. 5.6.2 | All required services are performed within the specified time requirements | 0 | random by the COR |
| Fall Protection Plan Para. 5.6.4 | All required services are performed within the specified time requirements | 0 | random by the COR |
| Lockout / Tagout Procedures Para. 5.6.6 | All required services are performed within the specified time requirements | 0 | random by the COR |
| Confined Space Para 5.6.7 | All required services are performed within the specified time requirements | 0 | 100% by the COR |
| Hazards Communication Plan Para 5.6.8 | All required services are performed within the specified time requirements | 0 | random by the COR |
| Asbestos Training Para 5.7.8 | All required training is completed within the specified time requirements | 0 | 100% by the COR |
| Portable Water System Para 5.7.11 | All required testing is completed within the specified time requirements | 0 | random by the COR |
| Reporting Environmental Compliance Para 5.7.12 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Reporting Sustainable Purchasing Practices Para 5.7.12 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Contractor Pandemic Plan Para 5.7.13 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Reporting Utility Meters Para 5.8 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Reporting BAS Deficiencies Para 5.10.1 | All required services are performed within the specified time requirements | 5 | 100% by the COR |
| Tour Plan Para 5.12.1 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Proactive Facility Tour Para 5.12.2 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Work Order Summary Report Para 5.14.1 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Emergency Work Orders Para 5.14.2 | Work order completion is in accordance with the Service Level Agreement in the CMMS | 0 | 100% BY THE COR |
| Emergency Callback Work Orders Para 5.14.3 | Work order completion is in accordance with the Service Level Agreement in the CMMS | 0 | 100% BY THE COR |
| Urgent Work Orders Para 5.14.4 | Work order completion is in accordance with the Service Level Agreement in the CMMS | 0 | 100% BY THE COR |
| Routine Work Orders Para 5.14.5 | Work order completion is in accordance with the Service Level Agreement in the CMMS | 0 | random by the COR |
| Low Priority Work Orders Para 5.14.6 | Work order completion is in accordance with the Service Level Agreement in the CMMS | 0 | random by the COR |
| Miscellaneous Work Para 5.16.2 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Monthly Report Para 5.17 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Predictive and Preventive Maintenance Plan Para 6.1 | The required plan is submitted and approved by the COR within the specified time requirements | 5 | 100% BY THE COR |
| Predictive and Preventive Maintenance Plan Para 6.1 | All required maintenance is accomplished per the plan and service is accepted by COR | 5 | random by the COR |
| HVAC Water Management Plan Para 6.6.1 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Emergency Power Equipment Testing and Inspection Para 6.10.4 | All required services are performed within the specified time requirements | 5 | random by the COR |
| Roof Anchorages Para 6.13.7 | All required services are performed within the specified time requirements | 0 | random by the COR |
| Initial Deficiency report Para 7.1 | All required services are performed within the specified time requirements | 5 | 100% by the COR |

# Technical Exhibit 2

# Deliverables Schedule

| Deliverable | Frequency | # Of Copies | Medium/Format | Submit To |
| --- | --- | --- | --- | --- |
| 1.6.1 Quality Control | 30 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.13.1 PM Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.13.1 Alternate PM Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.13.2 Onsite Supervisor. Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.13.2 Alternate Onsite Supervisor. Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.13.3 Safety Manager Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.14.1 Fire Alarm Tech Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.14.2 BAS Tech Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.14.3 Journeyman Electrician Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.14.4 Journeyman HVAC Tech Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.14.5 Cafeteria Equipment Tech Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.14.6 Journeyman Plumber Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.14.7 Journeyman Elevator Mechanic Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.14.8 General Maint. Mechanic Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.14.9 Operations / Admin Specialist Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.14.10 Journeyman HV Electrician Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.12.11 Locksmith Resume | 14 calendar days before Contract start date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.21.4 Phase-In Period Report | Within 10 business days of Phase-In period commencement | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 1.6.21.6 Phase -Out Period Plan | No less than 90 calendar days prior to the contract end date | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 5.3 Building Operating Plan | No later than the end of the Phase-In period and annually thereafter or when changes occur | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.4 Equipment Inventory | No later than the end of the Phase-In period and annually thereafter | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.6.2 Workplace Safety and Health Program | Within 30 calendar days of contract start date | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.6.4 Fall Protection Plan | Within 30 calendar days of contract start date | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.6.6 Lockout / Tagout Procedures | Within 30 calendar days of contract start date | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.6.7 Confined Space Plan | Within 60 calendar days of contract start date | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.6.8 Hazards Communication Plan | Within 30 calendar days of contract start date and annually thereafter on 30 Sep of each year | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.7.8 Asbestos Management Training | Within 5 days of training completion | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.7.11 Potable water system | Annually | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.7.12 Reporting Environmental Compliance | Annually | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.7.12 Reporting Sustainable Purchasing Practices | Annually | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.7.13 Contractor Pandemic Plan | No later than the end of the Phase-In period | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.8.3 Utility Consumption | Monthly | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.10.1 Reporting BAS Deficiencies | Monthly | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.12.3 Tour Plan | No later than the end of the Phase-In period | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.12.3 Proactive Facility Tour Report | Daily | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.14.1 Work Order Summary Report | Weekly | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.15.2.4 Indirect Costs (Markup) Percentage | As part of Contractor’s proposal | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |
| 5.15.6 ASWR Schedule | Within 10 calendar days of task order award and weekly thereafter | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.16.2 Miscellaneous Work | Monthly | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 5.17 Monthly Report | Monthly | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 6.1 Predictive and Preventative Maintenance Plan | Outline plan as part of Contractor’s proposal and completed plan not later than the end of the Phase-In period | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 6.6.1 HVAC Water Management Plan | No later than the end of the Phase-In period | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 6.6.5 Water Testing Results | Monthly | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 6.10 Emergency Power Equipment Reports | Per the approved predictive and preventive maintenance plan | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 6.13.7 Roof anchorages | Annually | 1 Original | Email / PDF or MS Office (preferred) | COR |
| 7.1 Initial Deficiency Report | With 30 calendar days of contract award | 1 Original | Email / PDF or MS Office (preferred) | CO and COR |

# Technical Exhibit 3

# Building Information Sheet

The following are building statistics for informational purposes only. The figures below are estimates only. When necessary, the COR or their designee will provide access to facility drawings.

Building Name	Frances Perkins Building

Building Number	DC0116ZZ

Age of Building	Constructed in 1974

Number of floors	6 above ground + 1 below ground

Normal Building Duty Hours	6:00am – 6:00pm, Monday - Friday, except holidays

Normal Building Operating Hours	24/7/365

Number of Agencies Housed	One (U.S. Department of Labor)

Usable Square Feet	973,778 SF

Rentable Square Feet	1,373,328 SF

Gross Square Feet	1,850,911 SF

Amenities	Child Development Center with Playground

Full-Service Cafeteria

Coffee Bar

24/7 Snack Bar

Fitness Center

Technical Exhibit 4

2025 PM Guide Cards

See Attachment

Technical Exhibit 5

Building Operating Plan (BOP) Template

See Attachment