STATEMENT OF WORK

Switchboard and Motor Control Center (MCC) Panel Replacement Service

17 February 2026

1.0 Scope.  This Statement of Work (SOW) defines the contractual requirements for the removal of one (1) Westinghouse switchboard and Motor Control Center (MCC) panel located in RM 241, and one (1) General Electric (GE) switchboard to include associated Motor Control Center (MCC) panel located in RM 119, and provide customized installation of one (1) Eaton (or equal) switchboard and Motor Control Center (MCC) panel located in RM 241, and one (1) Eaton (or equal) switchboard and Motor Control Center (MCC) panel located in RM 119 located within the ALTESS data center located on site in Radford, VA 24141-1061.

1.1 Background. In the late 1940s, the Army completed construction of a secure subterranean facility designed to offer comprehensive protection for classified operations. This facility was established as an Army-classified site to support a wide range of undisclosed missions, including those connected to foreign conflicts and other critical assignments. Over time, as the Army's operational scope broadened and mission requirements evolved, the facility faced increasing technological, environmental, and logistical demands. This growth necessitated improvements in data storage and processing capabilities, the installation of backup systems, and the expansion of support personnel.

In 1959, the Army relocated ALTESS to the Radford Army Ammunition Plant, selecting the site for its security and its established infrastructure. The facility offered a fully functional, covered, and protected environment suitable for classified military operations.

The existing infrastructure at the ALTESS facility includes General Electric (GE) and Westinghouse switchboards and motor control center (MCC) panels, along with related equipment. These components were installed between 1960 and 1970 and have continued to operate for decades. However, they have now reached the end of their useful life due to outdated technology and the increasing difficulty of sourcing replacement parts. While periodic repairs and partial refurbishments have extended their operational lifespan, the equipment’s age and obsolescence have made comprehensive replacement necessary.

The customized switchboards and MCC panels are specifically designed to be compatible with the ALTESS data center infrastructure, minimizing the risk of operational disruptions and maximizing the reliability of power distribution and control. This compatibility encompasses associated equipment and systems such as; switchgears for routing main power to and from backup generation equipment, facility chiller equipment—including water booster pumps, transfer pumps, well pumps, all hot water pumps, all air handler units, both fresh air intakes—sewer ejection systems, and cooling tower exhaust fans, which support the electrical systems for HVAC and IT cooling. Additionally, the equipment integrates with facility fusing switchboards for all electrical receptacles within the data center. All these systems are tied into the building automation system, which utilizes customized software designed to ensure seamless coordination and unified operation. This integration allows the various components—electrical, HVAC, plumbing, and IT cooling—to function together efficiently, providing centralized monitoring and control that enhances reliability, simplifies maintenance, and optimizes facility performance.

2.0 Applicable Documents.  N/A

3.0 Requirements.

3.1 The Contractor shall provide removal of one (1) Westinghouse switchboard and Motor Control Center (MCC) panel located in RM 241, and one (1) GE switchboard to include associated Motor Control Center (MCC) panel located in RM 119, and provide customized installation of one (1) Eaton (or equal) switchboard and Motor Control Center (MCC) panel located in RM 241, and one (1) Eaton (or equal) switchboard and Motor Control Center (MCC) panel located in RM 119 located within the ALTESS data center located on site in Radford, VA 24141-1061.

3.1.1 Specific Tasks:

3.1.1.1. GE Fused Switchboard and Motor Control Center (MCC): GE fused switchboard and motor control center (MCC) panel replacement service shall include:

Room 119 Equipment Removal & Installation Services:

- Removal of existing GE Fused Switchboard and MCC panel and all associated components.

- Disconnect two (2) hot water pumps from GE MCC during removal.

  - Hot water pumps must be temporally powered via alternate source until new MCC panel is operational. Hot water pumps will be reconnected to new MCC and functionally tested.

    - Enclosed starters must be provided (if applicable)

- Removal of all feeder circuits from GE switchboard to GE MCC.

- Through circuits identified during demolition shall be rerouted to maintain operation of assigned equipment.

  - One (1) circuit passes through to feed the Air Handler Unit (AHU) -1, and its associated CTs and Trane controls integration components shall be moved.

- All old unused control circuits within MCC shall be removed back to their origination points.

  - Identified control circuits will be going to the existing Powers Controls hand-off-auto (HOA) board in RM 119.

- All controls wiring, current transformers (CTs), and components supporting Trane Building Automation System (BAS) and/or Schneider Electric StruxureWare monitoring systems shall be kept intact and reinstalled into new MCC panel.

  - All work tied to the BAS system shall only be verified and recommissioned by a certified Trane Authorized Controls technician to include full functional testing.

  - All Schneider Electric StruxureWare monitoring systems metering components shall be verified and functional tested prior to project completed and installation of new MCC.

- Removal of all HOAs from the Powers Controls HOA board in RM 119.

- Installation of a one (1) new customized Eaton (or equal) Switchboard and MCC Panels

- Install new HOAs into new MCC doors of associated buckets.

- Installation of a new MCC panel.

  - Panel to include sufficient amount of motor starter buckets (approximately 11 current active).

    - Panel to supply all current loads, and additional feeder buckets to refeed six (6) existing lighting panel feeds from the GE Switchboard (five (5) existing 200A feeds and one (1) existing 100A feed), and provisional spots for future equipment.

- Refeed new MCC overhead from 800A breaker to existing 208v Square-D panel in RM 119.

- Disconnect and reroute six (6) existing lighting panel feeds using the GE switchboard as a junction box to reconnect to new MCC panel.

  - Upon reconnection, old GE switchboard shall be covered by sheet metal.

    - All work and repowering the six (6) existing panels from the new MCC shall be done after hours, on weekends when the facility is not occupied.

3.1.1.2. Westinghouse Fused Switchboard and Motor Control Center (MCC): Westinghouse fused switchboard and motor control center (MCC) panel replacement service shall include:

Room 241 Equipment Removal & Installation Services:

- Removal of existing Westinghouse Fused Switchboard and MCC panel and all associated components.

- Disconnect two (2) hot water pumps and two (2) existing sewer ejection compressors from existing Westinghouse fused switchboard MCC panel during removal.

  - Hot water pumps and sewer ejection compressors must be temporally powered via alternate source until new MCC panel is operational. Hot water pumps will be reconnected to new MCC and functionally tested.

    - Enclosed starters must be provided (if applicable)

- Removal of all feeder circuits between the Westinghouse switchboard and MCC.

- Through circuits identified during demolition shall be rerouted to maintain operation of assigned equipment.

- All controls wiring, CTs, and components supporting Trane Building Automation System (BAS) and/or Schneider Electric StruxureWare monitoring systems shall be kept intact and reinstalled into new MCC panel.

  - All work tied to the BAS system shall only be verified and recommissioned by a certified Trane Authorized Controls technician to include full functional testing.

  - All Schneider Electric StruxureWare monitoring systems metering components shall be verified and functional tested prior to project completed and installation of new MCC.

    - Most HOAs controlling equipment within the MCC tie back to Johnson Control HOAs in RM 241.

- Installation of one (1) new customized Eaton (or equal) Switchboard and MCC Panels

- Installation of a new MCC panel.

  - Panel to include sufficient amount of motor starter buckets (approximately fourteen (14) current active).

    - Panel to supply all current loads, and additional feeder buckets to refeed four (4) existing lighting panel feeds and Johnson Control Panel feed from Westinghouse Switchboard (four (4) existing 200A feeds and one (1) existing 50A feed), and two (2) provisional spots for future equipment.

- All HOAs shall remain in Johnson Controls HOA panel in RM 241 and wired back to the associated equipment MCC buckets that currently exist.

  - All controls and wiring associated with the Trane Building Automation System (BAS) shall be kept intact and reinstalled into the new MCC panel.  All related work shall only be verified and recommissioned by a certified Trane Authorized Controls technician to include full functional testing upon completion of service.

- Refeed new MCC overhead from 800A breaker to existing 208v Square-D panel in RM 119.

- Disconnect and reroute four (4) existing lighting panel feeds from the Westinghouse Switchboard (four (4) existing 200A feeds) with the feeder buckets into the new MCC.

  - Upon reconnection, old Westinghouse switchboard shall be removed and properly disposed of.

    - All work and repowering the four (4) existing panels from the new MCC shall be done afterhours, on weekends when the facility is not occupied.

3.1.1.3 Contractor shall provide arc flash, short circuit, and coordination study for the entire ALTESS facility including new equipment provided within this service.

3.1.1.4 Disposal: All GE and Westinghouse fused switchboards, panels, wiring, and harnesses to include any associated debris and parts shall be removed and disposed of at an and approved offsite federal, state, and local disposal site by contractor.

3.1.2 Hours of Operation:  The contractor is responsible for conducting business between the hours of 7:00am to 4:00pm, Monday thru Friday except Federal holidays or when the Government facility is closed due to local or national emergencies, administrative closings, weather, or similar Government directed facility closings. Work expected to be performed outside of these hours must be approved by the Government at least one week in advance.

For other than firm fixed price contracts, the contractor will not be reimbursed when the government facility is closed for the above reasons. The Contractor must at all times maintain an adequate workforce for the uninterrupted performance of all tasks defined within this SOW when the Government facility is not closed for the above reasons. When hiring personnel, the Contractor shall keep in mind that the stability and continuity of the workforce are essential.

Repowering of all panels shall take place after hours on weekends, hours to be outlined between contractor and government upon service completion.

3.1.3 The Contractor is required to perform services, if needed, on the following holidays:

New Year’s Day				Labor Day

Martin Luther King Jr.’s Birthday		Columbus Day

President’s Day				Veteran’s Day

Memorial Day				Thanksgiving Day

Independence Day				Christmas Day

Juneteenth National Independence Day

3.3 Delivery Requirements.

3.3.1 The contractor shall be responsible for any required services that include disposal, shipments, handling and delivery of any products and support associated with this requirement to the locations specified below. Delivery of this requirement shall be upon date specified by availability from manufacturer via awardee to the government representative at ALTESS.

3.3.1.1 Delivery Location.  Services shall be provided within the following location:

ALTESS

Radford Army Ammunition Plant

450 Constitution Road

Bldg. 450

Radford, VA 24141

DODAAC: W50DTZ

3.3.1.2 Primary Points of Contact. The primary POCs for this effort for any questions pertaining to the requirement are listed below:

Alternate Technical Point of Contact:

Tim Hancock

Facilities Operation Lead

Phone: 520-706-0273

Email: timothy.w.hancock.civ@army.mil

Requirement Point of Contact (POC):

Alison McCraw

Contracting Officer Representative (COR)

Phone: (520) 706-0045

Email: alison.j.mccraw.civ@army.mil

3.4 Period of Performance.  The Period of Performance (POP) shall be 5/1/2026 – 4/30/2027.

4. Security. Installation Access:  Access to U.S. installations, buildings and controlled areas is limited to personnel who meet security criteria and are authorized. Failure to submit required information/data and obtain required documentation or clearances will be grounds for denying access to U.S. installations, buildings, and controlled areas. The Contractor shall ensure that any subcontractors used in performance of this contract complies with these requirements and that all employees, of both the Contractor and any subcontractor utilized by the Contractor, are made aware of and comply with these requirements.

The Contractor shall be aware of and comply with the requirements associated with Installation Access Control. The Government is not liable for any costs associated with performance delays due solely to a firm’s failure to comply with Installation Access Control System (IACS) processing requirements.

The Contractor shall return installation passes to the issuing IACS office when the contract is completed or when a Contractor employee no longer requires access.

4.1 Background Checks: Contractor(s) and service personnel visiting or accessing the Radford Army Ammunition Plant (RFAAP) must have US citizenship and provide one form of photo ID that includes a valid real ID for entrance onto RFAAP. All personnel shall be escorted at all times.

All contractors and service personnel providing a recurring service to the RFAAP installation are required to obtain a RFAAP badge.  In order to obtain a RFAAP badge the contractor shall submit and obtain a favorable nationwide formal background investigation for the personnel. This background investigation must be conducted by a state agency or licensed background firm and not a computer search. Contractor personnel cannot have any adjudication actions (parole, probation, or open case files) within the past 5 years, or they will not be able to obtain a RFAAP badge and access to the installation shall be denied. The investigation shall be submitted to RFAAP security personnel though the contracting official. The RFAAP Security Office shall then, upon validation of the favorable investigation, provide the RFAAP badge.   The personnel receiving a RFAAP badge shall be required to carry the badge with them at all times while on the installation and secure the badge out of sight when not on the installation. Cell phones, cameras, PDA, and electronic devices are not allowed on the installation without prior approval.

Contractors not requiring an RFAAP badge must obtain a visitor’s badge at the Visitor Station located at the entrance to the RFAAP facility. This badge must be worn at all times and be plainly visible.

Contractor personnel performing work under this contract must possess and abide by the security requirements at the time of proposal submission, and must maintain the level of security required for the life of the contract

4.2. Contractor Identification Badges: Contractor personnel shall be easily identifiable through the display of badges IAW Contractor Identification (AE Reg. 27-715). The Contractor (to include subcontractors) shall provide each of their employees with an easily readable identification badge. The badge must include the employee’s name, the contractor’s company name, the functional area of assignment, and a recent color photograph of the employee. Companies with U.S. Government contracts will require their employees to wear these badges visibly when performing work at Government workplaces unless this would be impractical because of mission or safety considerations. The Contractor shall collect all ID Badges upon completion of the contract or termination of employee. A listing of issued ID cards shall be furnished to the Contracting Officer prior to the contract performance date and updated as needed to reflect Contractor personnel changes.

4.2 Physical Security:  The Contractor shall safeguard all Government equipment, information, and property provided for Contractor use. At the close of each work period, Government facilities, equipment, and materials shall be secured IAW the Army Physical Security Program AR 190-13.

4.3 Operations Security (OPSEC) Requirements: Contractor personnel shall adhere to facility security policies and restrictions. The Contractor shall immediately report suspicious activities to security personnel.

5.   ACRONYMS: Although not inclusive of every term used within this SOW, or that may be included in an acquisition, the following provides a list of acronyms commonly used in the acquisition field.

ACOR			Alternate Contracting Officer's Representative

AFARS		Army Federal Acquisition Regulation Supplement

ALTESS		Acquisitions Logistics & Technology Enterprise Systems & Services

ANSI			American National Standards Institute

AOR			Area of Responsibility

AR			Army Regulation

ASTM			American Society For Testing and Materials

AT			Anti-terrorism

ATCTS		Army Training Certification Tracking System

CAC			Common Access Card

CCE			Contracting Center of Excellence

CFR			Code of Federal Regulations

CONUS		Continental United States (excludes Alaska and Hawaii)

COR			Contracting Officer’s Representative

COTS			Commercial-Off-the-Shelf

DA			Department of the Army

DD250		Department of Defense Form 250 (Receiving Report)

DEAC			Diesel Engine Antifreeze Coolant

DFARS		Defense Federal Acquisition Regulation Supplement

DMDC			Defense Manpower Data Center

DoD			Department of Defense

EDC			Enduring Data Center

ELC			Extended Life Coolant

ESC			Extended Service Coverage

FAR			Federal Acquisition Regulation

GFP			Government Furnished Property

HLO			High Level Objective

HIPAA		Health Insurance Portability and Accountability Act of 1996

IA			Information Awareness

IAC			Installation Access Control

IACO			Installation Access Control Office

ID			Identification

IT			Information Technology

JVS			Joint Verification System

KO			Contracting Officer

OCI			Organizational Conflict of Interest

ODC 			Other Direct Costs

OPSEC		Operations Security

PA			Property Administrator

PII			Personally Identifiable Information

POC			Point of Contact

PRS			Performance Requirements Summary

PWS			Performance Work Statement

QA			Quality Assurance

QAP			Quality Assurance Program

QASP			Quality Assurance Surveillance Plan

QC			Quality Control

QCP			Quality Control Program

RA			Requiring Activity

RFAAP		Radford Army Ammunition Plant

RCO			Regional Contracting Office

SIGE			Safety and Health Protection Plan

TE			Technical Exhibit

USAG                      United States Army Garrison

UOM 			Unit of Measure