### SALIENT CHARACTERISTICS

Requirement: 15-Ton Commercial DX Split System (Condensing Unit and Air Handling Unit)

System-Wide Compatibility Requirements

- System Certification: The proposed condensing unit and air handling unit must be an AHRI-certified (Air-Conditioning, Heating, and Refrigeration Institute) matched set to ensure seamless operation as a single engineered unit.

- Nominal Capacity: The system must provide a nominal cooling capacity of 15 Tons (approximately 180,000 BTU/hr).

- Refrigerant Type: The system must utilize a modern, EPA-compliant, low-GWP refrigerant (e.g., R-410A or R-454B). The use of R-22 or transitional "drop-in" replacements is strictly prohibited.

- Power Supply: The equipment must operate on the facility's existing electrical service, which is 208/230V, 3-Phase, 60Hz.

- Energy Efficiency: The system must meet or exceed current Department of Energy (DOE) minimum SEER/IEER efficiency ratings for commercial 15-ton equipment.

Air-Cooled Condensing Unit (Outdoor Unit) Requirements

- Compressor Design: The unit must utilize scroll compressor technology equipped with internal thermal overload protection and high/low-pressure safety switches.

- Condenser Coils: Coils must be of microchannel or copper tube/aluminum fin construction and treated for corrosion resistance.

- Physical Protection: The unit must be equipped with factory-installed louvered panels or hail guards to protect the condenser coils from physical damage.

- Ambient Operation: The unit must be rated to operate efficiently in high ambient summer temperatures up to 115 degrees Fahrenheit.

Air Handling Unit (Indoor Unit) Requirements

- Cabinet Construction: The cabinet must be constructed of galvanized steel and be adequately insulated (double-wall or insulated single-wall) to prevent external condensation during operation.

- Blower Motor: The unit must feature a motor (belt-driven or direct-drive) capable of meeting or exceeding the existing ductwork's static pressure and CFM (Cubic Feet per Minute) requirements.

- Coil Type: The unit must feature a Direct Expansion (DX) evaporator coil equipped with a thermal expansion valve (TXV) or electronic expansion valve (EEV).

- Filtration: The unit must include a factory-installed filter rack capable of accommodating standard 2-inch pleated filters, with a minimum rating of MERV 8.

Controls and Automation Requirements

- DDC Integration: The system must include a factory-installed or field-provided Direct Digital Control (DDC) package.

- Open Architecture: The control system must allow full monitoring, setpoint adjustment, and scheduling by the 502nd Civil Engineer Squadron without requiring proprietary software gateways or recurring, brand-specific software licenses