580-25-101 Replace Upgrade Campus Overhead Paging System

Project No: 580-25-101

Scope of Work

- Foreword

  - Contractor shall provide all labor, materials, tools, equipment, expertise,

administration, supervision, and transportation as necessary to perform all work in accordance with provided construction specifications, drawings, all documents attached to this contract, all terms and conditions of this contract, and this statement of work.

  - This document does not relieve the contractor of their professional responsibility to comply with all local and federal construction and environmental codes and to perform and complete a fully coordinated job.

- General Project Description

  - Contractor shall completely prepare construction area for operations, including demolition and removal of existing finishes, assemblies, and systems, and furnish labor and materials and perform work for the installation of the new IP/SIP Overhead Paging System and removal of the existing analog Paging System as required by drawings and specifications. Work will be accomplished in phases and across multiple buildings on campus.

  - Work includes construction labor and supervision for architectural, demolition work including asbestos abatement, electrical, telecommunications and other work as required by the provided construction documents. This Scope of Work is not considered to be a comprehensive description of work details for this project. All work shall be completed per the plans/drawings and specifications.

- General Construction Requirements

  - Prior to any mobilization and construction, the contractor shall request and have an approved Infection Control Construction Permit, Construction Safety Plan, and an Interim Life Safety Measures Certification from the VAMC. Also project/construction schedule, schedule of values/prices and construction phases have to be provided and approved by VA’s COR/Project Engineer and/or Contracting Officer.

  - Contractor shall completely prepare site, prior to the installation of the equipment, and furnish labor, equipment and materials to perform work for this specific project as required by construction documents.

  - The entire project’s associated construction and temporary works shall conform to the latest VA specifications, VA Standards, energy conservation methods, EPA, OSHA, NFPA, NEC, ASHRAE, LIFE SAFETY CODE, UBC, local, Federal and industry requirements and regulations.

  - Project Record Drawings:  The Contractor will maintain a set of Record Drawings.  The Contractor will maintain a set of construction documents (field as-built drawings) to record actual construction changes during the construction process.  The project record drawings will be available for review by the VA Project Manager at all times.

  - The following milestone dates shall be incorporated into the contractor’s schedule.

    - Submittal Schedule and log shall be provided within ten (10) calendar days after Notice to Proceed. The contractor shall provide it to the Contracting Officer’s Representative (COR) for approval and shall include the dates for submission of Shop Drawings, Product Data, and Samples.

    - The Contractor shall submit a construction schedule within ten (10) calendar days after Notice to Proceed. The construction schedule shall be prepared in terms of calendar days (not working days). Once the construction schedule is submitted by the Contractor and approved by the CO, no lateness in the schedule shall be tolerated without the CO’s approval.

    - A pre-construction meeting shall be held within ten (10) calendar days after award of Contract. During the construction, the Contractor shall attend all weekly construction progress meetings. The meeting schedule and place will be discussed in the pre-construction meeting.

- General Contract Requirement

  - VA’s Normal Working Hours are 7:00 am to 4:30 p.m., Monday through Friday. Contractor shall coordinate work with the COR in order to not disrupt the end user’s operations which may include work earlier or later in the day and on weekends or federal holidays with at no additional cost to the VA. Noise disturbances and utility shutdowns/tie-ins shall be coordinated with the COR and not interfere with VA daily operations.

  - Pursuant to clause 52.236-8 Other Contracts incorporated by reference under section 4.33 52.252-2 Clauses Incorporated by Reference, Contractor shall fully cooperate with the other contractors and with Government employees and shall carefully adapt scheduling and performing the work under this contract to accommodate the additional work, heeding any direction that may be provided by the Contracting Officer. If required by the Contracting Officer, Contractor shall, at no additional cost to the VA, coordinate with other VA’s activities including but not limited to construction activities near the job site to ensure the construction work under this project will be in harmony with those activities. This coordination shall include but not limited to the careful scheduling of work commencement, equipment mobilization etc.

  - The following legal holidays are observed by this Government Agency:

New Year's Day			January 1st

Martin Luther King's Birthday	Third Monday in January

Presidents Day			Third Monday in February

Memorial Day				Last Monday in May

Juneteenth Independence Day		June 19th

Independence Day			July 4th

Labor Day				First Monday in September

Columbus Day			Second Monday in October

Veterans Day				November 11th

Thanksgiving Day			4th Thursday in November

Christmas Day				December 25th

and any day declared by the federal government as holiday.

- Project Meetings

  - Each week the contractor shall hold a progress meeting to review progress to date and to resolve all questions for the upcoming week. The progress meeting shall include at a minimum, the Project Manager and the Superintendent representing the Contractor, the COR and the CO representing the Government. Technical supervisor (foreman), sub-contractors, suppliers, etc. shall attend when requested by the Contracting Officer. The meeting shall be same day, time, and place each week.

  - Meeting Minutes - The contractor shall take minutes of all meetings held relative to this project. The format must be acceptable to the Contracting Officer (CO). Minutes must include the meeting date and time; agenda; meeting location; list of participants with their affiliations, and telephone numbers; be fully descriptive of issues, problems and decisions made; and action items with names of responsible parties and deadlines. In addition, the minutes must include, as attachments, all exhibits and references distributed as handout materials, unless the materials are part of a formal submission. The contractor shall provide, via e-mail, complete copies of all minutes to all attendees within 72 hours of the meeting. All challenges to the minutes will be reflected in a revised version prepared by the contractor and CO along with the contractor and COR shall sign/initial the minutes. In the event of any disputes or challenges that can’t be resolved, the Contracting Officer shall render a final decision. Copies of updated minutes shall be distributed to all attendees within 48 hours after change notice.

- Safety and Security

  - Contract workers under this project may require a VA issued identification card before the start of construction work at the Houston VAMC. There is no charge for the badges; however, multiple trips to MEDVAMC facility maybe required.

  - Contract employees, including all subcontractor employees, must be TB tested and receive a flu shot (each year under the contract performance) if they will work within the VA Hospital Building 100. A letter from the prime contractor shall be submitted to the CO prior to work commencing that all staff members are TB negative and the flu shot was received.

  - All contract personnel are subject to inspection of personal effects when entering or leaving the project site.

  - Parking is rigidly controlled throughout the Medical Center. Contractor parking is only allowed in authorized areas. Contractor shall abide by all police requirements.  Parking in designated patient parking areas is strictly prohibited. Parking for unloading equipment necessary to perform the work will be authorized in advance by the COR prior to starting the project.

--- End---