PERFORMANCE WORK STATEMENT (PWS)

PREVENTIVE MAINTENANCE AND REPAIR SERVICES FOR HVAC WATER CHILLERS AND AIR HANDLING UNITS AT THE VA CARIBBEAN HEALTHCARE SYSTEM

- Introduction.  This is a non-personal services contract to provide Preventive Maintenance and Repair Services for HVAC Water Chillers and Air Handling Units (AHUs) at the VA Caribbean Healthcare System (VACHS). The government shall not exercise any supervision or control over the contract service providers performing the services herein. Such contract service providers shall be accountable solely to the contractor who, in turn, is responsible to the government. The contractor shall provide all personnel, equipment, supplies, facilities, transportation, tools, materials, supervision, and other items and non-personal services necessary to perform the required service at VACHS as defined in this Performance Work Statement (PWS), section three (3.0), except for those items specified as Government-furnished property and services.  The contractor shall perform to the standards of this PWS.

  - Scope.  The Contractor shall perform all services in accordance with this PWS, Original Equipment Manufacturer (OEM) requirements, manufacturer manuals, and all applicable local, state, and federal laws and regulations, including Department of Veterans Affairs (VA) requirements. In the event of a conflict between regulatory guidance, the most stringent requirement shall apply. The scope includes, but is not limited to, providing preventive maintenance, inspections, adjustments, testing, and repair services for HVAC water chillers and air handling units (AHUs). See performance requirements in Section 3.0.

- General Requirements.  This section defines the general performance, administrative, and compliance requirements the Contractor shall follow throughout the performance of this contract. These requirements apply to all tasks described in this Performance Work Statement (PWS) unless otherwise specified.

  - Non-Personal Services.  The Government shall neither supervise contractor employees nor control the method by which the contractor performs the required tasks. Under no circumstances shall the Government assign tasks to, or prepare work schedules for, individual contractor employees. It shall be the responsibility of the contractor to manage its employees and to guard against any actions that are of the nature of personal services or give the perception of personal services. If the contractor believes that any actions constitute, or are perceived to constitute personal services, it shall be the contractor's responsibility to notify the Contracting Officer (CO) immediately.

    - Type of Contract.  The Government will award a firm-fixed price requirements type contract.

    - Period of Performance.  The period of performance for this effort will be an ordering period of five (5) years. In addition, the resulting contract will have an additional option to extend the services for up to six (6) months at the government’s discretion.

    - Location and Hours of Work. The contractor shall perform services at VACHS during the core hours of operation, 7:00 AM to 4:00 PM, Monday through Friday, excluding Federal Holidays and any period when the facility is closed due to local or national emergencies, administrative directives, or other government‑ordered closures. The contractor shall maintain an adequate workforce to ensure uninterrupted performance of all tasks within this PWS during core hours, except when the facility is officially closed as noted above.

      - Certain tasks under this contract shall be performed during non‑core hours when required to avoid interference with patient care, clinical operations, or critical hospital functions. See Section 3.0 for additional requirements governing non‑core or after‑hours work.

    - Recognized Government Holidays.  The Contractor may not be required to work on the legal public holidays listed below.  Holidays occurring on weekends will be observed as directed by the published United States Office of Personnel Management (OPM) calendar.

New Year’s: 				Day 1 January

Martin Luther King Jr. Birthday: 	3rd Monday in January

Washington’s Birthday: 		3rd Monday in February

Good Friday: 				Friday preceding Easter Sunday

Memorial Day: 			Last Monday in May

Juneteenth:				19 June

Independence Day: 			4th of July

Labor Day: 				1st Monday in September

Columbus Day: 			2nd Monday in October

Veterans Day: 			11th of November

Thanksgiving Day: 			4th Thursday in November

Christmas Day: 			25 December

  - Business Relations. The contractor shall successfully integrate and coordinate all activities needed to execute the requirement. The contractor shall manage the timeliness, completeness, and quality of problem identification. The contractor shall provide corrective action plans, submittals, timely identification of issues, and effective management of subcontractors, if any. The contractor shall seek to ensure customer satisfaction and professional and ethical behavior of all contractor personnel. Within the bounds of acquisition policy, the VACHS intends to work to find solutions that will be beneficial to both the Government and its Contractors.

  - Contract Administration and Management

    - Post Award Conference/Performance Evaluation Meetings.  Post Award Conference / Performance Evaluation Meetings.  The Contractor may be required to attend a post-award conference held by the contracting activity in accordance with RFO Part 42. This meeting may occur virtually or in writing.

      - Performance/Progress Meetings. Performance or progress meetings will be held as needed. Either party may request additional meetings to reconfirm expectations or address any Quality Control (QC) deficiencies that require corrective action. The Contractor Representative shall meet with the PPOC and/or Contracting Officer as required. Both parties will work together to resolve identified issues. The Contractor shall record, prepare, and distribute meeting minutes within three (3) business days after each meeting.

      - Contracting Officer (CO). The CO is the only person authorized to direct changes in any of the requirements under this contract, and, notwithstanding any provisions contained elsewhere in this contract, said authority remains solely in the CO.  In the event the contractor effects any such change at the direction of any person other than the CO, the change will be considered to have been made without authority and solely at the risk of the contractor. All contract administration will be effected by the CO. Communications pertaining to contractual administrative matters shall be addressed to the CO. No changes in or deviation from the terms and conditions shall be effected without a written modification to the contract, executed by the CO authorizing such changes.

      - Program Point of Contact (PPOC). The Program Point of Contact (PPOC) is the Government’s primary representative responsible for day‑to‑day program oversight and coordination for this contract. The PPOC serves as the functional equivalent of a COR and also fulfills the duties of the Government Program Manager. The PPOC monitors and assesses contractor performance, verifies that services are delivered in accordance with contract requirements, facilitates the exchange of technical information, and provides program‑level guidance to support successful contract execution. The PPOC is not authorized to change the terms or conditions of the contract. One or more Alternate PPOCs may be designated to perform these duties in the PPOC’s absence.

    - Contractor Employees. The contractor shall accomplish the assigned work by employing and utilizing qualified and certified personnel with appropriate combinations of education, training, and experience. The contractor shall match personnel skills to the work specified herein. The contractor shall ensure the labor categories/occupation code as defined by the Department of Labor are aligned with those tasks delineated in this PWS. The contractor shall comply with the minimum rates established in the applicable wage determination for this service. The Contractor shall provide the necessary resources and infrastructure to manage, perform, and administer the contract.

      - Contractor Identification. All contract personnel shall be clearly identified as Contractor personnel (e.g., badge, company logo, or uniform). Contract personnel must identify themselves in a manner that prevents any impression that they are Government employees. All correspondence, documents, emails, and reports produced by the Contractor shall be appropriately labeled as Contractor products or shall clearly disclose Contractor participation.

      - Contractor personnel performing work under this contract may be issued a PIV card, Non‑PIV badge, and/or Flash badge as required by the VA Caribbean Healthcare System (VACHS). These identification credentials are Government property and shall be worn and visibly displayed at all times while performing work within VACHS facilities. The Contractor shall ensure that all issued badges are returned immediately to the issuing office when no longer required, upon contract completion, or whenever a change in affiliation occurs.

      - The Contractor shall immediately notify the assigned VA sponsor and the VACHS Badging Office if any PIV, Non‑PIV, or Flash badge is lost, stolen, or damaged.

      - Contractor and subcontractor personnel may be required to complete mandatory VA training, including but not limited to information security, privacy, and facility‑specific safety or security courses. Mandatory annual training shall be completed as directed by VACHS, and all required online training will be provided at no cost to the contractor.

    - Key Personnel.  The contractor shall provide a single point of contact to administer this contract.  All key personnel shall have means of verbal and e-mail communication with the PPOC.  Key personnel and alternates must be able to communicate fluently in English both verbally and in writing.

    - Contractor Qualifications. The Contractor shall have at least five (5) years of experience in the maintenance of centrifugal, screw, scroll chillers, and AHUs.

    - Personnel Qualification:

      - Qualified Healthcare HVAC/Refrigeration Technician Lead. The Contractor shall designate a qualified healthcare HVAC/Refrigeration technician lead responsible for implementing ANSI/ASHRAE/ACCA Standard 180 maintenance procedures and ensuring alignment with the facility’s Ventilation Management Program in accordance with ASHRAE/ASHE Guideline 43. The lead shall oversee and verify completion of all HVAC and refrigeration tasks required under this PWS. The lead shall be present whenever the Contractor is performing services, except for call-back services.

      - Mechanical Engineer. A licensed Mechanical Engineer (PE) is not required for routine, daily, or standard preventive maintenance tasks performed under this contract. Oversight by a Mechanical Engineer is required only when the proposed work:

- Involves engineering calculations, design changes, or modifications that may affect ventilation parameters governed by ANSI/ASHRAE/ASHE Standard 170 (e.g., pressure differentials, air changes per hour, filtration levels); or

- Constitutes overhaul work or a major repair activity that may impact chiller capacity, AHU performance, system balance, or any HVAC parameter affecting clinical environmental conditions; or

- Requires system shutdowns, reconfigurations, or controls changes that may influence compliance with regulatory requirements or Joint Commission Environment of Care standards; or

- Involves a new installation or major modification that, by VA policy or applicable codes, must be reviewed, stamped, or supervised by a licensed Mechanical Engineer.

- Routine preventive maintenance (PM), minor repairs, and daily operational HVAC tasks do not require a mechanical engineer's involvement

        - The Contractor shall ensure that a Mechanical Engineer provides technical oversight, documentation, and professional certification only for the activities listed in 2.3.5.2.

      - Qualified Healthcare HVAC/Refrigeration Technicians.  Personnel providing services to the HVAC systems shall be licensed by the “Colegio de Técnicos de Refrigeración y Aire Acondicionado de Puerto Rico (CTRAPR)” or hold a refrigeration and air-conditioning technician license formally recognized for practice within Puerto Rico. Contractor personnel responsible for dismantling, repairing, relocating, modifying, maintaining, aligning, adjusting, lubricating, welding, or performing preventive maintenance and repair services on equipment covered under this contract shall possess a technical degree in Air Conditioning and Refrigeration and shall be experienced in the maintenance and repair of centrifugal, screw, scroll water chillers, and AHUs, as well as healthcare-specific HVAC components.

        - Technicians shall also be knowledgeable of ventilation requirements applicable to healthcare facilities, including those related to infection control, pressure relationships, and environmental support for clinically sensitive spaces.

      - Electricians. Contractor personnel responsible for the electrical installation, maintenance, troubleshooting, or repair of any electrical or electronic components associated with the equipment covered under this contract shall possess a technical degree in electrical or electromechanical technology and shall be licensed by the Colegio de Peritos Electricistas de Puerto Rico (CPEPR). A license issued by another U.S. jurisdiction is acceptable only if formally recognized for practice in Puerto Rico under applicable reciprocity provisions. All electrical work shall be performed exclusively by licensed electricians.

      - Sheet Metal / Duct Mechanic. The Contractor shall provide personnel qualified to perform installation, maintenance, modification, and repair of ductwork and sheet‑metal components associated with the HVAC systems covered under this contract. Personnel performing ductwork services shall possess documented training and experience in commercial or institutional sheet‑metal fabrication and installation, including work on air‑handling units, supply and return air ducts, plenums, access panels, and related components. Duct mechanics shall be capable of installing and sealing duct sections, fabricating transitions, repairing or replacing damaged sheet‑metal assemblies, and verifying proper airflow integrity in accordance with applicable mechanical codes, SMACNA standards, and VA Medical Center requirements. All ductwork modifications shall be performed in a manner that maintains required pressure relationships and supports infection control measures in healthcare environments.

      - OSHA Training. The contractor’s Qualified Healthcare HVAC/Refrigeration Technician Lead shall have a valid 30 Hrs. OSHA training course in Construction Safety & Health. All other personnel shall have OSHA 10 Training for General Industry & Construction.

    - Standards of Conduct.  Contractor personnel’s conduct shall not reflect discredit upon the Government.  The Contractor shall ensure that personnel present a professional appearance.  The Contractor's employees shall observe and comply with all local policies and procedures concerning fire, safety, environmental protection, sanitation, security, and possession of firearms or other lethal or illegal weapons or substances.  The Contractor is responsible for ensuring that any contractor employees providing services under this contract conduct themselves and perform services in a professional, safe, and responsible manner.  The contractor shall remove, from the job site, any employee for reasons of misconduct or security.  The contractor shall ensure employee conduct complies with 41 U.S.C. 423, Procurement Integrity.  The contractor shall also ensure that no contractor employees conduct politically related activities or events on VACHS facilities.

    - Contractor personnel and property shall be subject to search and seizure upon entering and leaving the confines of VACHS facilities. The Contractor shall be responsible for assuring that all personnel authorized to perform work under this contract obtain facilities’ access as required. The Contractor shall provide a personnel roster listing all employees who will work under this contract.  The roster listing shall be provided within 14 days of contract award.  Access to the VACHS facilities will be exclusively for work in connection with this contract.

    - The contractor is responsible for the supervision of all their employees while on government property. It is the Contractor's responsibility to ensure compliance with this PWS and the requirements referenced in this contract. Provisions provided in the PWS are not intended to relieve the Contractor of this responsibility.

  - Equipment Condition and Acceptance “as is”. The Contractor acknowledges that all Government‑owned HVAC equipment covered under this contract, including chillers, air‑handling units, pumps, controls, and associated components, is accepted “as is” at the start of the contract. The Contractor shall not claim additional compensation for pre‑existing conditions, age, deterioration, or prior maintenance history of the equipment. Any deficiencies discovered during initial inspection shall be reported to the Contracting Officer; however, such reporting does not relieve the Contractor of its responsibility to perform all preventive maintenance and repair services required under this PWS.

  - Vehicles. The contractor's vehicles shall be utilized solely for their designated purpose, maintained in operable condition, and comply with all local, state, and federal safety regulations. The vehicles shall be operated in accordance with all medical center traffic regulations and identified with the company name and logo. The contractor may have a maximum of two (2) vehicles at any given time on VACHS premises due to limited space.

  - Health and Safety.  The Contractor and its subcontractors shall comply with Public Law 91‑596 (OSHA) and 29 CFR 1910 and 29 CFR 1926, and all applicable federal, state, and local regulations protecting employees, building occupants, and the environment. The Contractor shall provide, within 14 calendar days of contract award, a job‑specific written Health and Safety Plan that includes:

- A Hazard Communication (HAZCOM) Program, compliant with 29 CFR 1910.1200, including chemical inventory, labeling, SDS access, and employee training.

- Lockout/Tagout (Energy Control) Program in accordance with 29 CFR 1910.147.

- Confined Space Entry Program, if applicable under 29 CFR 1910.146.

- Any additional written safety programs required by OSHA for the performance of this contract.

    - The plan shall be tailored to the specific HVAC tasks performed under this contract. The Government reserves the right to review and reject the plan if it is not compliant with applicable safety codes and regulations.

    - Occupants' Safety.  The contractor shall take all safety precautions and safety measurements necessary to protect the lives and health of occupants of the building and users of the equipment.  No process or materials shall be employed in such a manner that they will introduce additional hazards into occupied space.  In addition, shall have in place and be responsible for enforcing it, a safety program/procedure, which shall be followed by their employees in the performance of their duties.  The contractor shall maintain the premises in a safe and healthful condition according to applicable OSHA standards and all other requirements of this contract, including standards governing indoor air quality, the existence of mold and other biological hazards, and the presence of hazardous materials.

    - The Contractor shall comply with all applicable safety standards and codes for HVAC chiller and AHU maintenance and repairs, including:

- NFPA 70, National Electrical Code for fire and electrical safety in equipment design, installation, and inspection

- NFPA 99, Health Care Facilities Code to ensure safety of HVAC systems in a medical environment

- NFPA 101, Life Safety Code for fire protection measures and means of egress during emergencies

- OSHA standards covering electrical hazards, confined spaces, lockout/tagout, PPE, and fall protection relevant to HVAC work

- The Joint Commission’s Environment of Care criteria, ensuring safe utility systems, fire barriers, and HVAC safety procedures in healthcare facilities

    - In the performance of this contract, the Contractor shall follow Veterans Affairs Central Office (VACO) Directive 7710, Occupational Safety and Health, for safe work practices and take such safety precautions as the Safety Officer or designee may determine to be reasonably necessary to protect the lives and health of occupants of the building.  The Contractor shall comply with VACHS smoking policy, which designates all spaces as non-smoking areas.

    - The Contractor is responsible for identifying, providing, and maintaining, if required, all personal protective equipment (PPE) needed to perform the duties outlined in the contract.  In addition, the contractor is responsible for identifying and providing all applicable safety programs (i.e., lockout/tag out, universal precautions, etc.) required to perform the work. Training on required safety programs and the proper use of PPE shall be provided, and documentation shall be maintained by the contractor.

    - Hot Work Permit. The Contractor shall obtain a Hot Work Permit from the Safety Office whenever soldering, welding, using a cutting torch, or other open flame, spark, or heat-producing equipment. The contractor is required to follow ALL requirements outlined for the issuance of the Hot Work Permit.

  - Injury or Accident Reporting.  The Contractor shall maintain an accurate record of accidents resulting in injury or death and accidents resulting in damage to government property, supplies, and equipment.

    - As defined by OSHA, EPA, ANSI, and all other regulatory requirements, any incident of a major malfunction, accident, or injury, a written report shall be submitted by the Contractor to VACHS within five (5) working days following the incident. The report shall state the cause, what, where, and when, and why the incident happened, and the repairs and tests that were or are to be made to correct the cause of the incident.

    - Environmental Compliance.  The contractor shall comply with all environmental regulations and refrigerant‑handling requirements applicable to HVAC chiller and air‑handling unit services, including:

- EPA Section 608 of the Clean Air Act, including technician certification, refrigerant leak detection, recovery, recycling, reclamation, and required recordkeeping.

- ANSI standards applicable to environmental performance, refrigerant safety, and equipment integrity.

- VA environmental and HVAC design guidance, including requirements relating to refrigerant containment, disposal, and system integrity.

- All other federal, state, local, and facility environmental laws, regulations, rules, and environmental management plans that apply to HVAC operation, refrigerant handling, waste disposal, and environmental protection on VA property.

      - Safety Data Sheet. The Contractor shall submit to the government, prior to the start of the contract, Safety Data Sheets (SDS) for all potentially hazardous materials (including but not limited to lubricants, cleaners, refrigerants, solvents, working fluids, and chemicals) that will be brought into the facility under this contract. No chemical or hazardous material may be introduced into the facility without prior approval by the government. SDS for any new materials introduced after contract start shall be submitted concurrently with the material’s arrival on site. The Contractor shall maintain a copy of all SDS at the chemical storage location in an area accessible to government personnel, ensuring compliance with all federal, state, local, and facility “Right‑to‑Know” requirements.

      - Storm Drain System. Mechanical cleaning products can be drained through the sanitary piping by separating the solid material.  Materials that may clog or affect the sanitary piping shall not be discharged through the sanitary pipe system.  The contractor is responsible for discharges affecting the facility’s sanitary piping system.  The contractor will not discard, direct or indirect, any material as a result of the maintenance and repair of any equipment through the storm drain system.  The contractor is responsible for any illegal discharge through the storm drain system that may reach any natural water body. Failure to comply will render the contractor fully and solely liable for any resulting penalties, including fines or imprisonment, as imposed by local or federal environmental regulatory authorities.

      - Odor and Vapor Control. The Contractor shall implement measures to control odors, mist, vapors, and airborne irritants generated during maintenance, cleaning, repairs, or other work activities performed under this contract. Such measures shall be coordinated with VACHS to avoid disruption to patient care, ensure acceptable indoor air quality, and comply with facility infection control and safety requirements. When required, the Contractor shall use containment methods, local exhaust ventilation, filtration, or scheduling during non‑core hours to minimize exposure to building occupants.

  - Physical Security.  The Contractor shall protect existing buildings, facilities, utilities, and equipment during the working period and will be responsible for any damages resulting from the operation and/or execution of this contract.  The Contractor shall conduct his operations to cause the least possible interference with the normal operations of the government because the facilities will remain in operation during the entire maintenance period.

    - Key Control. The contractor shall be responsible for receiving, securing, issuing, and accounting for any keys issued for access to buildings, offices, equipment, gates, or other areas, for the purposes of this contract. Keys shall not be duplicated without the approval of the PPOC. If the contractor or its agents duplicate a key without permission of the PPOC, the contractor shall remove the individual(s) responsible from performing work under the contract. In the event that the contractor has lost any such keys, the contractor shall promptly notify the PPOC. In either case, the contractor shall reimburse the Government for the cost of rekeying that portion of the system so compromised. The contractor shall strictly prohibit contractor employees from opening locked areas to permit entrance of persons other than contractor employees engaged in the performance of assigned work in those areas, or personnel authorized entrance by the PPOC. Any occurrences of lost keys shall be immediately reported to the PPOC by the contractor.

  - Liability and Responsibility for Damaged Property.

    - Damage to Government Property.  The contractor shall be held responsible for cleaning up all spillage and/or leakage at no additional cost to the government.  The contractor shall be held liable for damage or destruction of Government property (e.g., buildings, vehicles, sidewalks, fences, etc.) caused by the contractor, contractor personnel, or representatives of the contractor in the performance of services on this contract.  The contractor shall submit their damage report to the PPOC within 24 hours of damage and shall include the repairs and corrective action plan, as applicable.  If the contractor fails to take the required corrective action, the government retains the right to exercise other rights or remedies available to the CO.

    - Damage to Privately-Owned Property.  The Contractor shall be held liable for damage or destruction of privately owned property (e.g., privately owned vehicles), as defined in this PWS, caused by the contractor, contractor personnel, or representatives of the contractor in the performance of services in this contract.  The contractor shall take corrective action within 5 working days to repair damages or replace destroyed property.  The contractor shall purchase and maintain at all times a general third-party liability insurance policy of not less than $500,000 per event coverage (See FAR Clause 52.228-5).

    - Damage Reports.  The contractor shall submit a damage report to the CO and designated representative within 24 hours of damage or destruction to government property or privately owned property caused by the contractor, contractor personnel or representatives of the contractor.  The damage report shall detail the facts and the extent of damages or destruction, and the corrective action taken by the contractor to repair damages or replace destroyed property.

  - Fraud, waste, and abuse.  The Contractor shall be responsible for maintaining proper conduct and good discipline within the contractor occupied work area(s).  Contractor personnel shall be encouraged to be alert to, and report suspected situations of fraud, waste, and abuse, or other intentionally dishonest conduct against the government observed during or in the performance of this contract.  The contractor lines of communication are with the PPOC and the CO.

  - Influenza vaccine.  “Flu Shot” is mandatory for all VHA employees and contractors as per VHA Directive 1192.0.  Contractor shall provide a list of employees under contract performance with their vaccination compliance.  This requirement is to be submitted annually, on or before November 30.  Employees and Contractors who are not vaccinated as per authorized exclusions on VHA Directive are to be documented as such and always required to wear healthcare face mask while on VHA premises.

  - Addition and/or removal of equipment, facilities (locations), work areas, and services.  The Government reserves the right to add and/or remove equipment, facilities, work areas, and services under this contract.  Due to ongoing construction projects, replacement of obsolete equipment, and other initiatives, which are affecting all equipment and facilities at VA locations (including leased facilities) within Puerto Rico and the U.S. Virgin Islands, adjustments to the contract terms and conditions, including adding/removing quantities, new equipment, and locations, may be necessary.  All changes, if required, will be executed through a written supplemental agreement in accordance with FAR 52.212-4(c).  Any contract modification and task order must be within the general scope of this contract and will not fundamentally alter the nature of the contract.

- Performance Requirements.  This section specifies the Performance Objectives and Performance Elements for this contract. The Contractor shall maintain chiller plant and AHU system availability at ≥98.5% overall, excluding Government‑directed shutdowns and Government‑approved planned maintenance outages. All other downtime, including contractor‑initiated or preventable equipment failures, shall be included in availability calculations. The Contractor shall use and install parts, including consumables, that are appropriate to the equipment, its operating conditions, and required performance levels. Substandard components shall not be used in Government equipment. All parts, materials, components, and replaceable inserts used in the maintenance and repair of equipment and systems in Federally controlled space shall be new, suitable for the type and severity of service, and shall meet applicable safety and performance codes and standards. Aftermarket parts are not permitted unless approved by the Government. The Contractor shall not manipulate valves, controls, automatic devices, lock‑out controls, or heat‑load transfer systems unless they have been released or secured by the Operations Control Center (OCC). The Contractor shall provide all personnel, equipment, supplies, facilities, transportation, tools, materials, supervision, and other items and non‑personal services necessary to perform Preventive Maintenance (PM), Corrective Maintenance (CM), and Repair Services for the following systems:

  - Preventive Maintenance (PM) and Repair Service to the Heating, Ventilation, and Air Conditioning (HVAC) Water Chillers.  The contractor shall perform all preventive maintenance and repair services necessary to keep the HVAC water chillers operating safely, efficiently, and in accordance with OEM instructions and applicable industry standards. Work includes maintaining and repairing major chiller components such as compressors, evaporators, expansion valves, condenser and evaporator coils, motors, fans, blowers, pumps, refrigerant piping and valves, control panels, sensors, strainers, safety devices, chilled-water and condenser-water piping, and vibration-isolation components. For chiller units that have operational redundancy, preventive maintenance and repair services under this section may be performed during core hours. See Technical Exhibit 1 (TE-1) for the complete list of covered equipment.

    - Equipment Condition and Maintenance Requirements. The contractor shall maintain all chiller equipment in reliable, first-class operating condition. Maintenance shall follow the OEM’s recommended procedures and frequencies, as well as applicable industry standards such as ASHRAE 15, ASHRAE 34, ASHRAE 180, Joint Commission EC.02.05.01. If a unit requires additional maintenance to remain safe, reliable, or compliant, the contractor shall perform that maintenance within this contract’s scope. The contractor is responsible for all covered equipment's operational condition throughout the contract period.

    - Replacement of Damaged or Defective Components. The contractor shall replace any damaged or defective mechanical or electrical components associated with the chiller system, up to the main electrical power disconnect. Replacement may include, but is not limited to, motors, condenser panels, purge system components, valves, heat exchangers, belts, gear assemblies, structural components, fan assemblies, strainers, piping, hangers, catwalk elements, filtration components, and lightning arresters. All components shall be maintained clean and fully operational per OEM instructions and industry best practices.

    - Chillers’ Scheduled Maintenance Program

      - Program Overview and Approval. The Contractor shall implement a scheduled maintenance program that ensures chiller plant reliability, energy efficiency, and compliance with hospital infection-control and safety standards. The program shall be approved by PPOC before implementation. Maintenance shall meet or exceed OEM recommendations and applicable standards (e.g., ASHRAE 170, ASHRAE 180, Joint Commission EC.02.05.01, etc.). The Contractor shall provide a written preventive maintenance program detailing methods, frequencies, and performance verification procedures.

      - Preventive Maintenance Tasks. The Contractor shall perform inspections, preventive maintenance (PM), and repairs in accordance with all OEM specifications and shall submit PM checklists for PPOC approval before work begins. PM tasks include, but are not limited to:

- Maintaining condenser and evaporator performance per OEM guidance; verifying approach temperature and cleaning when required.

- Monitoring refrigerant integrity monthly; repairing leaks promptly and maintaining EPA-compliant records.

- Cleaning each unit’s interior and exterior monthly and maintaining a minimum ten (10) foot radius around each unit free of debris, vegetation, trash, and any obstructions, including keeping all exposed piping, conduits, and associated lines clear of vegetation.

- Performing annual oil analysis; changing oil only when analysis indicates or as per the OEM recommended interval.

- Replacing oil filters and dryers in accordance with oil analysis results or OEM recommendations.

- Providing 24/7 emergency support.

- Performing repairs directly related to chiller operation.

- Providing crane services when required for major component handling.

- Maintaining and repairing pipe and chiller insulation up to 50 feet from the unit: Ensure no leaks and maintain insulation integrity.

- Verifying purge system operation as needed, but at least monthly.

- Following OEM maintenance manuals for all units listed in the agreement.

- Calibrating pressure gauges and thermometers annually and replacing damaged or out-of-tolerance instruments.

- Containing and properly disposing of debris generated during maintenance.

- Inspecting, adjusting, painting, and repairing guard rails, catwalks, ladders, piping, lightning arresters, and structural supports as needed.

- Performing all inspections and PM for chilled-water pumps, condenser-water pumps, and their motors on a monthly basis in accordance with manufacturer recommendations, including but not limited to bearings, couplings, seals, and pressure gauges.

- Daily Inspections. The Contractor shall conduct daily operational rounds of all chillers and document key operating parameters to verify continued performance in accordance with manufacturers’ standards and applicable industry requirements.

      - Specific Component Maintenance.

        - Condensers. The condensers shall be mechanically cleaned at least twice a year for water-cooled chillers and monthly for air-cooled chillers.  The contractor shall dispose of all debris removed from the condenser outside the facility. After completion of each mechanical cleaning, the contractor shall clean the pump strainer associated with the unit serviced, the condenser, and the evaporator side. In addition, the Contractor shall provide monthly service to the pump strainer to ensure proper flow and system performance.

        - Evaporators. The evaporators shall be mechanically cleaned at least once a year.

        - Chiller Repairs Identified During Preventive Maintenance. The Contractor shall identify, diagnose, and correct defective, worn, or failing parts and components discovered during the performance of scheduled preventive maintenance whenever practicable. Components subject to repair or replacement during preventive maintenance include, but are not limited to, belts, bearings, valves, sensors, purge system components, panels, and structural elements required to maintain proper chiller operation. Repairs discovered during preventive maintenance shall be completed during that same preventive maintenance service unless system shutdown constraints or safety conditions require rescheduling, in which case the Contractor shall notify the PPOC for coordination. All routine repairs included as part of preventive maintenance, including labor and standard parts, are covered under the firm-fixed-price PM/Repair CLIN and shall not incur additional labor charges.

        - Diagnostic Testing. When a component is determined through diagnostic testing, performance trending, or OEM evaluation to be beyond economical repair, the Contractor shall replace the component and restore the system to full operational performance as specified under this contract. All repair and replacement work shall be completed in a manner that minimizes downtime, maintains environmental and safety compliance, and supports continuous hospital operations.

        - Call‑Back Services. The Contractor shall provide 24/7 emergency call‑back response. All labor, materials, diagnostic efforts, overtime, travel, tools, and parts required to resolve call‑back issues shall be included in the firm-fixed price of the PM/Repair service. Call‑back service includes correction of failures, alarms, leaks, abnormal operation, and any condition that places the chiller system or associated equipment at risk of failure.

          - Emergency Contact Requirements. The Contractor shall provide the government with pertinent emergency telephone numbers in order to contact the contractor in case an emergency develops. At least one of the emergency telephone numbers shall be staffed and manned twenty-four (24) hours per day. This information shall be provided in writing to the government before the effective contract start date.

          - Call‑Back and Response Time. Upon notification by the Government of an abnormal condition, alarm, failure, or emergency with chiller equipment, the Contractor shall:

- Acknowledge the notification by telephone within thirty (30) minutes and initiate remote troubleshooting or guidance if possible.

- If the issue cannot be resolved remotely, the Contractor shall dispatch onsite personnel within two (2) hours of notification.

- All telephone call-backs, diagnostic efforts, and on-site responses shall be included in the provided at no additional cost to the Government and are included in the firm-fixed price of the PM/Repair service.

    - Major Overhaul of Centrifugal Compressors’ Assembly (task order-based work). The contractor shall perform major overhaul of the centrifugal compressors’ assembly. The overhaul shall include compressor teardown, bearing replacement, gasket/seal replacement, tube cleaning, leak testing, refrigerant recharge, alignment, and post-overhaul performance testing per OEM specifications.

    - Chillers Repair Work Beyond Standard PM Tasks. All repairs beyond the standard preventive maintenance tasks identified in this PWS shall be ordered and funded separately by the Government via task order. Repairs beyond PM may include, but are not limited to, replacement of motors, bearings, coils, valves, fans, electrical components, sensors, and other mechanical or control elements. Such repairs shall not be included in the firm-fixed-price PM/Repair CLIN and may only be performed with prior written authorization from the Contracting Officer, issued in the form of a task order or a modification to an existing task order. In emergencies where immediate action is required to protect life, safety, property, or critical hospital operations, the Contracting Officer may authorize the contractor to proceed verbally; however, a task order or modification shall be issued by the Contracting Officer as soon as practicable thereafter.

  - PM and Repair Service to Air Handling Units (AHUs). The Contractor shall ensure all Air Handling Units (AHUs) operate safely, reliably, and at optimal efficiency by providing all required preventive maintenance and repair services. The Contractor is responsible for performing inspections, preventive maintenance, and repairs in full compliance with all OEM specifications, industry standards, and applicable regulations. Prior to initiating any preventive maintenance, the Contractor shall submit PM checklists to the PPOC for approval. Required PM tasks include, but are not limited to, all actions necessary to maintain AHUs performance, safety, and environmental compliance. All preventive maintenance and repair services for AHUs shall be performed outside the core hours of operation identified in paragraph 2.1.3, unless otherwise approved by the Government. See Technical Exhibit 2 (TE 2) for the complete list of AHUs equipment.

    - Equipment Condition and Maintenance Requirements. The contractor shall maintain all AHUs equipment in reliable, first-class operating condition. Maintenance shall follow the OEM’s recommended procedures and frequencies, as well as applicable industry standards such as ASHRAE 170, ASHRAE 180, and any other applicable code(s). If a unit requires additional maintenance to remain safe, reliable, or compliant, the contractor shall perform that maintenance within this contract’s scope. The contractor is responsible for all covered equipment's operational condition throughout the contract period.

    - Replacement of Damaged or Defective Components. The contractor shall replace any damaged or defective mechanical or electrical components associated with the AHU system, up to the main electrical power disconnect. Replacement may include, but is not limited to, motors, belts, pulleys, bearings, fans, dampers, linkages, seals, filtration media, and structural components. All components shall be maintained clean and fully operational per OEM instructions and industry best practices.

    - AHUs Scheduled Maintenance Program.

      - Program Overview and Approval. The Contractor shall implement a scheduled maintenance program that ensures AHUs reliability, ventilation performance, and compliance with hospital infection-control and safety standards. The program shall be approved by the PPOC prior to implementation and shall meet or exceed the stricter of OEM recommendations and applicable standards (e.g., ASHRAE 180, ASHRAE 170, Joint Commission EC.02.05.01).

      - Preventive Maintenance Tasks. The Contractor shall perform inspections, PM, and repairs in accordance with all OEM specifications and shall submit PM checklists for PPOC approval before work begins. PM tasks include, but are not limited to:

- Maintaining AHUs performance per OEM guidance; verifying airflow, pressure relationships, and cleaning as required.

- Monitoring filtration media monthly; repairing leaks promptly and maintaining EPA-compliant records.

- Cleaning each unit’s interior and exterior monthly and maintaining a minimum five (5) foot radius around each unit free of debris, vegetation, trash, and any obstructions, including keeping all exposed piping, conduits, and associated lines clear of vegetation.

- Performing lubrication tasks for bearings.

- Replacing belts as needed.

- Providing 24/7 emergency support.

- Performing repairs directly related to AHU operation.

- Providing crane services when required for major component handling.

- Maintaining and repairing AHUs insulation.

- Verifying damper operation monthly and removing non-condensable issues as required.

- Following OEM maintenance manuals for all units listed in the agreement.

- Calibrating pressure gauges and thermometers as needed, but at least annually, and replacing damaged or out-of-tolerance instruments.

- Containing and properly disposing of debris generated during maintenance.

- Inspecting, adjusting, painting, and repairing guard rails, catwalks, ladders, piping, lightning arresters, and structural supports as needed.

- Performing all inspections and PM for fan assemblies and drive components as needed, but at least on a monthly basis in accordance with manufacturer recommendations, including bearings, couplings, seals, and other related items.

      - Specific Component Maintenance

        - Filtration Media. The Contractor shall maintain filtration media in accordance with the stricter of the filter manufacturer’s or the AHU manufacturer's recommendations, using filtration media that is OEM or OEM-approved equivalent meeting safety and performance codes. The Contractor shall ensure that filtration media meets required airflow, pressure-drop, and indoor air quality standards. Filters must be replaced whenever their condition fails to support the required system performance, reaches the maximum pressure differential specified by the OEM, or as per the stricter of the filter manufacturer’s or the AHU manufacturer's recommendations. If nearby construction or other environmental factors adversely affect filter performance, the Contractor shall increase the replacement frequency to ensure the filtration media continues to meet the required performance standards.

        - Lubrication. The Contractor shall perform and document pillow block bearing lubrication in accordance with the bearing manufacturer’s specifications and recommendations. Lubrication activities shall be included in the scheduled maintenance plan and completed at intervals necessary to ensure the bearings operate within required performance parameters.

        - Belt Maintenance. The Contractor shall maintain belt performance in accordance with the stricter of the belt manufacturer's or the AHU manufacturer's recommendations, using a belt that is equal to or better than what is recommended by the manufacturer. The Contractor shall ensure that belts meet system operational requirements and the equipment manufacturer's recommended procedures. Belts must be replaced whenever their condition fails to support the required system performance, or as per the stricter of the belt manufacturer's or the AHU manufacturer's recommendations.

        - Fan Assembly. The Contractor shall maintain fan assembly pulley performance in accordance with the equipment manufacturer's manuals and system design requirements. Pulley assemblies shall be inspected at least annually for wear, bearing degradation, alignment, and functionality. Pulley units shall be replaced when inspection or performance testing indicates they no longer support required system operation.

        - Cooling Coils. Cooling coils shall be maintained in accordance with equipment manufacturer requirements and system performance needs. Coils shall be cleaned at least once each month, or more frequently if inspection or performance testing indicates reduced airflow or heat‑transfer capability. If pressure washing is used, the Contractor shall ensure that water pressure does not exceed 800 PSI. The use of chemical cleaning agents is prohibited unless prior discussion and written approval are obtained from the PPOC. Any cooling coil determined to be unserviceable on the air‑side shall be replaced by the Contractor.

        - Replacement of Supply/Return Fan Assemblies (task order-based work). Under individual task orders, the Contractor shall replace supply fan assemblies and return fan assemblies for designated AHUs to ensure the required system performance. Replacement fan assemblies must match existing AHU configurations and performance requirements or meet approved equivalent standards. The Contractor shall properly remove, transport, and dispose of old fan assemblies in an environmentally compliant manner. The Contractor shall perform operational testing, vibration checks, and balancing as applicable, and shall verify that system performance meets OEM and system specifications after installation. The Contractor shall complete all required installation reports, test results, redlined drawings (if changes occur), and updates to O&M records. The Contractor shall adhere to all applicable safety protocols, including lockout/tagout procedures, confined space requirements, and facility‑specific safety rules. Prior to installation, the Contractor shall submit replacement component information, including model and performance specifications, for approval. The Contractor shall also coordinate outage windows, access requirements, and the sequence of work with the PPOC to minimize operational disruptions. This service shall be performed outside core hours unless otherwise approved by the PPOC.

The following AHUs and Return Air Fan (RAF) units contain multiple supply or return fan motors of varying horsepower. The Contractor shall account for these configurations during planning, submittal preparation, and execution of replacement work:

- AHUs with four (4) motors of 10 HP: Units 1, 9, 11, and 12

- AHUs with four (4) motors of 15 HP: Units 2, 3, 4, and 8

- AHUs with four (4) motors of 20 HP: Units 5, 6, 7, and 10

- RAF units with 20 HP motors: Units 1, 3, 4, 8, 9, 10, 11, and 12

- RAF units with 25 HP motors: Units 2, 5, 6, and 7

      - Comprehensive Maintenance. The Contractor shall ensure that the following components operate as designed and are maintained in accordance with OEM specifications and system performance requirements:

- Outside air dampers, linkages, seals, and components. Ensure optimal operation and compliance with performance standards.

- Return air dampers, linkages, seals, and components. Maintain required airflow and pressure relationships.

- Supply air dampers, linkages, seals, and components. Verify operational integrity and effectiveness.

- Unit enclosure. Maintain structural integrity and ensure cleanliness.

- Filtration media. Achieve required airflow, pressure-drop, and indoor air quality standards; replace as per the contract standards.

- Filtration racks. Ensure proper fitment and operational effectiveness.

- UV lights. Maintain functionality and operational compliance.

- Enclosure doors and seals, including access doors. Ensure proper sealing and accessibility.

- Unit’s insulation from enclosure and piping up to the main distribution branch. Maintain insulation effectiveness and condition.

- Fan assembly or components. Ensure operational performance consistent with design specifications.

- Unit’s drain. Maintain functionality to prevent blockages and ensure proper drainage.

- Drip pan. Ensure cleanliness and proper function to prevent overflow and contamination.

- Unit’s illumination lighting. Maintain operational and safety lighting standards.

- Arc arrestors or grounding mechanism. Ensure operational integrity and compliance with safety standards.

- Drive motors, pulleys, and belts. Maintain operational performance; replace as necessary.

- Ductwork and insulation up to 50 feet from the unit: Ensure no leaks and maintain insulation integrity. (Note: 50 feet is measured along the duct path from the AHU connection.)

- Instrumentation: Calibrate and maintain all pressure differential gauges, pressure gauges, temperature gauges, pitot tubes, actuators, and mechanical linkages.

- Structural supports: Inspect, adjust, paint, or repair any guard rail, catwalks, ladders, piping, and air handling unit’s structural support.

- Vibration analysis and monitoring. Conduct to detect early signs of wear or imbalances in fan assemblies and drive motors.

- Electrical inspections. Perform routine checks of connections, control panels, and wiring.

- Air quality testing and monitoring. Conduct to ensure compliance with health standards.

- Documentation and record-keeping: Maintain detailed logs of all maintenance activities, inspections, and repairs.

- Thermographic scanning. Utilize infrared thermography to detect overheating in electrical components, motors, and bearings.

- Leak detection: Regularly inspect and promptly repair any leaks in ductwork, seals, and piping.

- Conduct to ensure all safety mechanisms, such as emergency shut-offs, are functional and compliant with safety regulations.

    - AHUs Repairs Identified During Preventive Maintenance. The Contractor shall identify, diagnose, and correct defective, worn, or failing parts and components discovered during the performance of scheduled preventive maintenance whenever practicable. Components subject to repair or replacement during preventive maintenance include, but are not limited to, belts, bearings, valves, sensors, purge system components, panels, and structural elements required to maintain proper AHU operation. Repairs discovered during preventive maintenance shall be completed during that same preventive maintenance service unless system shutdown constraints or safety conditions require rescheduling, in which case the Contractor shall notify the PPOC for coordination. All routine repairs included as part of preventive maintenance, including labor and standard parts, are covered under the firm‑fixed‑price PM/Repair CLIN and shall not incur additional labor charges.

      - Diagnostic Testing. When a component is determined through diagnostic testing, performance trending, or OEM evaluation to be beyond economical repair, the Contractor shall replace the component and restore the system to full operational performance as specified under this contract. All repair and replacement work shall be completed in a manner that minimizes downtime, maintains environmental and safety compliance, and supports continuous hospital operations.

      - Call‑Back Services. The Contractor shall provide 24/7 emergency call‑back response. All labor, materials, diagnostic efforts, overtime, travel, tools, and parts required to resolve call‑back issues shall be included in the firm-fixed price of the PM/Repair service. Call‑back service includes correction of failures, alarms, leaks, abnormal operation, and any condition that places the AHUs system or associated equipment at risk of failure.

        - Emergency Contact Requirements. The Contractor shall provide the government with pertinent emergency telephone numbers in order to contact the contractor in case an emergency develops. At least one of the emergency telephone numbers shall be staffed and manned twenty-four (24) hours per day. This information shall be provided in writing to the government before the contract start date.

        - Call‑Back and Response Time. Upon notification by the Government of an abnormal condition, alarm, failure, or emergency with AHUs equipment, the Contractor shall:

- Acknowledge the notification by telephone within thirty (30) minutes and initiate remote troubleshooting or guidance if possible.

- If the issue cannot be resolved remotely, the Contractor shall dispatch onsite personnel within two (2) hours of notification.

- All telephone call-backs, diagnostic efforts, and on-site responses shall be included in the firm-fixed price of the PM/Repair service.

    - Repair Work Beyond Standard PM Tasks. All repairs beyond the standard preventive maintenance tasks identified in this PWS shall be ordered and funded separately by the Government via task order. Repairs beyond PM may include, but are not limited to, replacement of motors, bearings, coils, valves, fans, electrical components, sensors, and other mechanical or control elements. Such repairs shall not be included in the firm fixed price PM/Repair CLIN and may only be performed with prior written authorization from the Contracting Officer, issued in the form of a task order or a modification to an existing task order. In emergencies where immediate action is required to protect life, safety, property, or critical hospital operations, the Contracting Officer may authorize the contractor to proceed verbally; however, a task order or modification shall be issued by the Contracting Officer as soon as practicable thereafter.

    - Spot Coolers Relocation, Installation, and Removal. The Contractor shall relocate, position, install, connect, and place into operation Government‑furnished portable spot coolers whenever an Air Handling Unit (AHU) is shut down for preventive maintenance, corrective repair, or due to equipment malfunction. The Contractor shall ensure that each spot cooler is properly connected to the required electrical source and placed into functional operation as directed by the Government.

      - When the spot coolers are no longer required, the Contractor shall disconnect, uninstall, remove, and return all units to the designated Government storage area. The Contractor’s responsibilities include only the physical relocation, installation, operational setup, disconnection, and return of the units.

      - The Government will provide all spot coolers. The Contractor shall not be responsible for furnishing, repairing, maintaining, or servicing any spot coolers.

      - Coordination with the PPOC shall be required before installation or removal of any spot coolers to ensure appropriate deployment and retrieval aligned with hospital operational needs.

      - Spot coolers relocation, installation, operation, and removal services under PWS 3.2.6 are included in the PM firm-fixed price.

  - Sheet Metal and Ductwork (beyond what is covered by chillers and AHUs sections above). In addition to the 50 feet covered, the Contractor is not required to provide routine maintenance and repair services for sheet metal and ductwork beyond this range. Any additional work related to sheet metal and ductwork beyond the initial 50 feet from chillers and AHUs will be ordered via a task order on an as‑needed basis. Paragraph 3.3 may also be applied to other HVAC‑related equipment not included in the preventive maintenance requirements of paragraphs 3.1 and 3.2.

    - General Requirements for Task-Order Ductwork Services. When requested via task order, the Contractor shall be responsible for the following tasks related to sheet metal and ductwork systems: repairs, corrections, improvements, additions, etc.

    - Task Order-Based Work. All services related to sheet metal and ductwork beyond the initial 50 feet from AHUs will be provided only upon issuance of a task order. These tasks include, but are not limited to:

- Inspecting Ductwork. Conduct inspections to identify leaks, damage, and insulation integrity.

- Sealing Duct Leaks. Detect and seal duct leaks promptly to ensure optimal system performance.

- Insulation Maintenance. Inspect, repair, and replace insulation as necessary to maintain energy efficiency and system performance.

- Adjusting and Aligning Dampers. Ensure all dampers are functional and maintain balanced airflow throughout the ductwork system.

    - Standards and Guidelines. All work performed under task orders must adhere to the following standards and guidelines:

      - OEM’s Recommended Procedures: Follow the Original Equipment Manufacturer’s (OEM) recommended procedures for all tasks.

      - SMACNA Guidelines. Comply with Sheet Metal and Air Conditioning Contractors' National Association (SMACNA) standards for duct construction and HVAC systems.

      - ASHRAE Standards: Including ASHRAE 90.1 (Energy Standard for Buildings Except Low-Rise Residential Buildings) and ASHRAE 62.1 (Ventilation for Acceptable Indoor Air Quality).

      - NFPA Standards. Particularly NFPA 90A (Standard for the Installation of Air-Conditioning and Ventilating Systems).

    - Repairs and Corrections. The Contractor shall perform repairs and corrections to any damaged or defective ductwork components as identified in a task order. This includes, but is not limited to:

      - Fixing Leaks. Seal air leaks in ductwork to prevent air loss and maintain HVAC efficiency.

      - Replacing Sections: Replace damaged or deteriorated sections of ductwork with new materials that meet OEM specifications and industry standards.

      - Repairing Insulation. Fix any compromised insulation to restore thermal performance and energy efficiency.

    - Improvements and Additions. Improvements and additions to the ductwork system will be provided when required and ordered via task order. This includes:

      - System Upgrades. Upgrade ductwork materials or design to improve airflow, reduce noise, and enhance overall system efficiency.

      - New Installations. Add new duct runs, branches, or components to accommodate facility expansions or layout changes.

      - Dampers and Controls. Install new or upgraded dampers and control systems to improve airflow management and system responsiveness.

    - Documentation and Reporting. The Contractor shall maintain detailed records for any work performed under task orders. This documentation shall include:

      - Inspection Reports. Document findings from ductwork inspections, including identified issues and recommended actions.

      - Repair Records. Documentation of all repairs and corrections, including parts replaced, outcomes, and any other pertinent information.

      - Improvement and Addition Reports. Provide detailed reports on any improvements or additions made to the ductwork system, including design changes and performance impacts.

  - Trailer-Mounted Chiller Contingency Support. In the event of an unforeseen failure, system outage, or operational condition that poses an immediate risk to the continuity of facility operations, the Government may require the Contractor to provide a trailer‑mounted chiller or equivalent temporary cooling solution. This requirement is included within the general scope of the contract; however, the Contractor is not required to provide pricing at the time of contract award.

    - If such temporary equipment becomes necessary, the Contractor shall provide the Government with a written quote that includes all associated costs, such as delivery, installation, connection, operation, fuel or power requirements, maintenance during the rental period, removal, and return transportation. The Government may negotiate the proposed price and terms.

    - A supplemental agreement may be executed to incorporate the mutually agreed pricing into the contract, and a separate task order may be issued to define the specific scope of work, period of performance, responsibilities, and technical requirements. Prior to issuing any contract modification or task order for a trailer‑mounted chiller, the Contracting Officer shall complete a fair and reasonable price determination.

    - Nothing in section 3.4 obligates the Government to rent a trailer‑mounted chiller, nor does it obligate the Contractor to furnish such equipment without a separately issued task order and executed supplemental agreement.

  - Filter Supply Requirements (Contract Line Item 0005 and Sub-Line Items 0005AA–0005AF). The Contractor shall deliver the filters identified under SLINs 0005AA–0005AF to the designated warehouse/location upon issuance of a delivery order. These line items are supply‑only requirements, are not considered services, and are not subject to the Service Contract Act. No installation or disposal is required, as these filters support equipment outside the PM services under this contract. Quantities in TE‑3 are for evaluation only and shall not be construed as minimum or maximum purchase obligations.

- Performance Requirements Summary (PRS) Matrix

  - The Contractor service requirements are summarized into performance objectives that relate directly to mission essential items.  The performance threshold briefly describes the minimum acceptable levels of service required for each requirement.  These thresholds are critical to mission success.  The government expects the contractor to perform at a minimum, the identified acceptable levels throughout the life of the contract, and the contractor’s performance shall be given significant consideration when evaluating recommendations for future government contracts and/or awards.

  - Method of Surveillance: The Government performs surveillance to determine if the Contractor exceeds, meets, or does not meet these standards. The Government shall use these standards to determine Contractor performance and shall compare Contractor performance to the Acceptable Quality Level (AQL). Surveillance methods may include: random, planned, 100% inspections, and/or customer complaints.

| PRS # | Performance Objective | Performance Standard | Acceptable Quality Level | Surveillance Method | Remedies |
| --- | --- | --- | --- | --- | --- |
| 1 | Chiller Plant and AHUs availability ≥98.5% overall | PWS Paragraph 3.0 | ≥98.5% acceptable level | As per PWS paragraph 4.2 | As per PWS paragraphs 4.4, 4.4.1 |
| 2 | Preventive Maintenance – Chillers & AHUs ≥98.5% overall | PWS Paragraph 3.1, 3.2 | ≥98.5% acceptable level | As per PWS paragraph 4.2 | As per PWS paragraphs 4.4, 4.4.1 |
| 3 | Major Overhaul of Centrifugal Compressors’ Assembly | PWS Paragraph 3.1.4 | 100% acceptable level | As per PWS paragraph 4.2 | As per PWS paragraphs 4.4, 4.4.1 |
| 4 | Emergency Call‑Back Service & Response Chillers & AHUs Acknowledge within 30 minutes, dispatch within 2 hours | PWS Paragraphs 3.1.3.4.2, 3.2.4.2 | 99% acceptable level | As per PWS paragraph 4.2 | As per PWS paragraphs 4.4, 4.4.1 |
| 5 | Repairs Identified During Preventive Maintenance – Chillers & AHUs | PWS Paragraphs 3.1.3.4, 3.2.4 | 95% acceptable level | As per PWS paragraph 4.2 | As per PWS paragraphs 4.4, 4.4.1 |
| 6 | Repair Work Beyond Standard PM Tasks – Chillers & AHUs | PWS Paragraph 3.1.5, 3.2.5 | 95% acceptable level | As per PWS paragraph 4.2 | As per PWS paragraphs 4.4, 4.4.1 |
| 7 | Spot Coolers – Relocation/Installation/Removal | PWS Paragraph 3.2.6 | 98% acceptable level | As per PWS paragraph 4.2 | As per PWS paragraphs 4.4, 4.4.1 |
| 8 | Sheet Metal & Ductwork | PWS Paragraph 3.3 | 98% acceptable level | As per PWS paragraph 4.2 | As per PWS paragraphs 4.4, 4.4.1 |
| 9 | Trailer-Mounted Chiller Contingency Support | PWS Paragraph 3.4 | 98% acceptable level | As per PWS paragraph 4.2 | As per PWS paragraphs 4.4, 4.4.1 |
| 10 | Filter Supply Requirements (CLIN 0005) | PWS Paragraph 3.5 | 98% acceptable level | As per PWS paragraph 4.2 | As per PWS paragraphs 4.4, 4.4.1 |

  - Quality Assurance.  The Government will evaluate the Contractor’s performance under the contract, IAW the PRS Matrix.  The Government retains the right to inspect and test all services called for by the contract.  The Government will conduct inspections and tests in a manner that will not unduly delay the work.  If any of the services performed do not conform to contract requirements, the Government may require the Contractor to perform the services again in conformity with contract requirements, at no increase in contract amount.

  - Whenever the PPOC notifies the contractor of any deficiencies detected in the work performed, the contractor shall correct cited deficiencies within 3 days, or as otherwise authorized by the PPOC, after the notification by the PPOC, without affecting the regularly scheduled work.

    - Certain contract requirements, including but not limited to OEM‑required interval services, preventive maintenance tasks, statutory testing intervals, and performance standards such as system availability, are time‑sensitive and cannot be re‑performed for credit once the required timeframe or performance period has passed. If the Contractor fails to meet any such requirement within the prescribed interval or performance period, the service shall be considered a non‑recoverable performance failure. The Government may document such failures in the Contractor Performance Assessment Reporting System (CPARS) and apply any other remedies permitted under the contract.

  - Upon satisfactory completion by the Contractor and acceptance by the PPOC of the work completed by the contractor in accordance with this Performance Work Statement, payment will be approved.  Failure to complete the work stated in this PWS may result in unfavorable Contractor Performance Assessment Reporting System (CPARS) ratings and/or deductions to be determined by the CO.

  - Quality Control.  The contractor shall develop and maintain an effective Quality Control Program (QCP) to ensure services are performed IAW this PWS.  The Contractor shall provide, within 14 calendar days of contract award, a job‑specific written QCP. The purpose of this program is to identify, prevent, and ensure non-recurrence of defective services.  At a minimum, the program shall include the following:

- The name(s) of the individual(s) who will perform the services described in the contract.

- A checklist used in the inspection and performance verification during the performance of the service. The checklist shall include every requirement included in the manufacturers’ manual(s), updates, notices, and any other requirement from accrediting organizations such as ASHRAE 180 and EC.02.05.01 or agencies, as well as every task required to be performed.

- A schedule of the dates programmed for the service requested.

- A system for identifying and correcting deficiencies in the quality of services before the level of performance becomes unacceptable and/or the PPOC identifies the deficiencies.

- In addition to providing the documentation at the end of each service, the contractor is responsible for maintaining the required documents of all the services conducted by the Contractor and the corrective actions taken. All documentation shall be made available to the Government during the term of the contract.

- Deliverables

| Deliverable | Frequency | # of Copies | Medium/Format | Distribution | Applicable PWS Paragraph |
| --- | --- | --- | --- | --- | --- |
| Certificate of Liability | Within 10 days after contract award | 1 | PDF/Word | PPOC | RFO 52.228-5 |
| Meeting Minutes | Within 3 business days after each meeting | 1 | Word | CO / PPOC | 2.3.1.1 |
| Employee Roster | Within 14 days after contract award | 1 | PDF/Word | PPOC | 2.3.7 |
| Health and Safety Plan | Within 14 days after contract award | 1 | PDF/Word | PPOC | 2.6, 2.6.1 |
| Damage Reports | Within 24 hours of the event | 1 | PDF | CO / PPOC | 2.9.1, 2.9.2, 2.9.3 |
| Influenza Vaccine | Annually (on or before November 30) | 1 | PDF/Word | PPOC | 2.11 |
| Chillers & AHUs Scheduled Maintenance Program | At the beginning of the contract | 1 | PDF/Word | PPOC | 3.1.3, 3.2.3 |
| Chillers and AHUs Monthly Reporting | Within five (5) days after the end of the month | 1 | PDF | PPOC | 3.1.5.4.1, 3.2.5.4.1 |
| Quality Control Plan | Within 14 days after contract award | 1 | PDF/Word | PPOC | 4.6 |

- Related Documents

  - Definitions

AVAILABILITY: “Availability” means the chiller plant and AHU system are fully operational and capable of meeting the required load. Government‑directed outages and Government‑approved planned maintenance periods are excluded from downtime calculations. All other downtime, including unscheduled outages or failures resulting from inadequate maintenance, shall be included.

CONTRACTING OFFICER (CO):  A Contracting Officer is a government employee who has authority to enter into, administer, and or terminate contracts, as well as make related determinations and findings on behalf of the Government.  (Note: The only individual who can legally bind the Government.)

Program Point of Contact (PPOC) - A representative from the requiring activity appointed by the CO to perform surveillance and to act as liaison to the contractor

CONTRACTOR:  A supplier or vendor awarded a contract to provide specific supplies or service to the Government.  The term used in this contract refers to the prime.

DEFECTIVE SERVICE:  A service output that does not meet the standard of performance associated with it in the Performance Work Statement

DELIVERABLE:  A tangible or intangible object produced as a result of the project that is intended to be delivered to a customer (either internal or external).  Examples of a deliverable are a report, a document, a server upgrade, or any other building block of an overall project.

FISCAL YEAR: A period beginning on October 1 and ending September 30 of the consecutive calendar year.  The fiscal year is designated by the calendar year in which it ends.

GOVERNMENT FURNISHED PROPERTY (GFP): All equipment, goods and land possessed by the government and subsequently delivered or otherwise made available to the Contractor.

INSPECTION. Examining and testing supplies or services (including, when appropriate, raw materials, components, and intermediates assemblies) to determine whether they conform to contract requirements

MATERIAL. Property that may be consumed or expended during the performance of a contract, component parts of a higher assembly, or items that lose their individual identity through incorporation into an end-item. Material does not include equipment, special tooling, and special test equipment or real property.

MINOR DISCREPANCIES.  Problems identified during maintenance checks that do not require significant time or significant materials to correct, such as loose wires or belts, hoses, clamps, coolant additives and other minor adjustments.

NON-PERSONAL SERVICES. The personnel rendering the services are not subject, either by the contract's terms or by the manner of its administration, to the supervision and control usually prevailing in relationships between the government and its employees. Non personal service contracts are authorized by the government in accordance with FAR 37.012, under general contracting authority, and do not require specific statutory authorization.

OCCUPATIONAL SAFETY AND HEALTH ADMINISTRATION (OSHA). Government agency part of the US Department of Labor with the primary responsibility for administrating the Occupational Safety and Health act of 1970.  This act has the purpose of preservation of human resource.

OVERHAUL. An overhaul is a comprehensive restoration of the existing chiller in which critical internal components are disassembled, inspected, repaired, or replaced to return the unit to OEM‑recommended performance and reliability levels. The overhaul extends equipment service life but retains the original chiller framework and serial number. It typically includes tasks such as compressor teardown, tube cleaning, bearing replacement, gasket renewal, leak testing, recharging refrigerant, and full operational testing.

PHYSICAL SECURITY. Actions that prevent the loss or damage of Government property.

PROPERTY. All tangible property, both real and personal.

QUALITY ASSURANCE (QA):  A procedure or set of procedures taken by the Government to ensure that services acquired under government contracts conform to the contract’s quality and quality requirements.

QUALITY ASSURANCE SURVEILLANCE PLAN (QASP):  A plan specifying the surveillance methodology used by the PPOC for surveillance of the contractor’s performance.

QUALITY CONTROL (QC):  Task performed by the contractor to ensure excellence of the organization’s output.

REPAIR.  The correction of a malfunction or non-conformance that cannot be accomplished without significant time and/or material, as determined by the PPOC.

SUBCONTRACTOR.  One that enters into a contract with a prime contractor. The Government does not have privity of contract with the subcontractor.

TASK ORDER-BASED WORK. Refers to work that is not part of the contract’s recurring or routine maintenance services. This work is performed only when specifically requested by the Government. Each instance of work is authorized through a separate task order, or by modifying an existing task order via a supplemental agreement. The task order defines the scope, deliverables, schedule, and pricing for that particular requirement. No task order‑based work may be performed without the issuance of a formal task order.

  - Acronyms

ANSI		American National Standards Institute

ASHRAE	American Society of Heating, Refrigerating and Air-Conditioning Engineers

CA		Corrective Action

CAP		Corrective Action Plan

CDR		Contract Discrepancy Report

CFR		Code of Federal Regulations

CPARS	Contractor Performance Assessment Reporting System

EPA		U.S. Environmental Protection Agency

FAR		Federal Acquisition Regulation

FFP		Firm-Fixed Price

FY 		Fiscal Year

IAW		In Accordance With

CO		Contracting Officer

NCO		Network Contracting Office

NFPA		National Fire Protection Association

NLT		No Later Than

OSH		Occupational Safety and Health

OSHA		Occupational Safety and Health Act

POC		Point of Contact

PPOC		Program Point of Contact

PR		Puerto Rico

PRS		Performance Requirements Summary

PWS		Performance Work Statement

QA		Quality Assurance

QASP		Quality Assurance Surveillance Plan

QC		Quality Control

RAF		Return Air Fan

RFO		Revolutionary FAR Overhaul

SMACNA	Sheet Metal and Air Conditioning Contractors' National Association

TE		Technical Exhibit

TJE		The Joint Commission

VA		Veterans Affairs

VAAR		VA Acquisition Regulation

VACHS	Veterans Affairs Caribbean Healthcare System

VACO		Veterans Affairs Central Office

VHA 		Veterans Health Administration

  - Applicable Directives and Publications

The following laws, regulations, policies, and procedures in effect on the date of contract issuance and all subsequent changes or updates apply:

29 CFR, Part 1910 			Occupational Safety and Health Standards

29 CFR, Part 1926			Safety and Health Regulations for Construction

38 U.S.C. §5725 	Liquidated Damages for Data Breaches involving SPI

ANSI/ASHRAE/ASHE Guideline 43	Ventilation Management Program

ASHRAE 15	Safety Standards for Refrigeration Systems

ASHRAE 34	Refrigerant Designations

ASHRAE 170	Ventilation of Health Care Facilities

ASHRAE 180 	Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems

EC.02.05.01	Joint Commission Utility Systems

EPA Clean Air Act	Environmental Protection Agency Clean Air Act Section 608

FIPS PUB 201-3	Personal Identity Verification (PIV) of Federal Employees and Contractors

HSPD 12	Homeland Security Presidential Directive 12 Policy for a Common Identification Standard for Federal

Employees and Contractor

NFPA 70				National Electrical Code

NFPA 90A	Standard for the Installation of Air‑Conditioning and Ventilating Systems

NFPA 99				Health Care Facilities

NFPA 101				Life Safety Code

OMB M-05-24				Office of Management and Budget (OMB) Guidance

Implementation of Homeland Security Presidential Directive (HSPD) 12 – Policy for a Common Identification Standard for Federal Employees and Contractors

SMACNA Standards			SMACNA HVAC Duct Construction Standards

VA Directive & Handbook 0710	Personnel Suitability and Security Program

VACO Directive 7710			Occupational Safety and Health

VHA Directive 1192.0	Influenza Vaccination Program for VHA Health Care Personnel

TECHNICAL EXHIBIT 1 (TE-1)

HVAC Water Chillers Equipment Schedule

| Location | Qty | Manufacturer | Model Number | VA Property Number |
| --- | --- | --- | --- | --- |
| Out-Patient Building | 1 | Trane | CVHE500, Centrifugal Chiller | 65205052 |
|  | 1 | Trane | CVHE500, Centrifugal Chiller | 65205051 |
|  | 1 | Trane | CVHE570, Centrifugal Chiller | 65227457 |
|  | 1 | Trane | CVHE570, Centrifugal Chiller | 65227458 |
|  | 1 | MULTISTACK | MS(020/70x)C2H2H2AAR410A | 65243723 |
|  | 1 | MULTISTACK | MS(020/70x)C2H2H2AAR410A | 65243725 |
| Community Living Center | 1 | Trane | CGAM090F | 65228258 |
|  | 1 | Trane | CGAM090F | 65228259 |
| Main Chiller Plant | 1 | Trane | CVHF1470NA4L0GS0316E, Centrifugal Chiller | 65220473 |
| Main Chiller Plant | 1 | Trane | CVHF1470NA4L0GS0316E, Centrifugal Chiller | 65222793 |
| Main Chiller Plant | 1 | Trane | CVHF1470NA4L0GS0316E, Centrifugal Chiller | 65222794 |
| Main Building Surgery | 1 | Trane | CVHF360, Centrifugal Chiller |  |
| South Bed Tower | 1 | York | YKESESQ6-CNGS, Centrifugal Chiller | 65218635 |
| South Bed Tower | 1 | York | YKESESQ6-CNGS, Centrifugal Chiller | 65218636 |
| MRI CT Scan | 1 | Trane | CGAM 052F 2L03 | 65244958 |
| MRI CT Scan | 1 | Trane | CGAM 052F 2L03 | 65244957 |
| Linear Accelerator | 1 | Filtrine Manufacturing | PCP-150S-160A-WF | 65244966 |
| Building 1 PET/CT | 1 | KKT Kraus | KPC 108-L-U/S | 65242993 |
| CT/MRI | 1 | HASKRIS | HB35357-0001, OUTDOOR OPC24-A7-AHXXXX | 65247609 |
| SICU | 1 | Trane | CGAM 110F |  |
| Main Chiller Plant | 3 | Taco | TC121014DGRAA4D2MZB0887D | 65264366 / 65264365 / 65264364 |
| Main Chiller Plant | 3 | Taco | TC100816DLUAA4C2MZB0946D | 65264363 / 65264363 / 65264363 |
| OPA | 3 | ITT BARTON INSTRUMENTS | 150 | 65178324 / 65178326 / 65178321 / 65178323 |
| OPA | 3 | BELL & GOSSETT | 6BC | 65227466 / 65227465 / 65227464 |
| OPA | 5 | BELL & GOSSETT | 6E SERIES 1510 | 65227470 / 65227469 / 65227468 / 65227461 / 65227460 |
| OPA | 4 | BELL & GOSSETT | 3E SERIES 1510 | 65227472 / 65227471 / 65227463 / 65227462 |
| SBT | 2 | WESTINGHOUSE | AEHH8P | 65218631 / 65218632 |
| SBT | 2 | BELL & GOSSETT | TEOUX0000950 | 65218638 / 65218637 |
| CLC | 4 | Unknown |  | 65156800 / 65156801 / 65156802 / 65156803 |
| CT/MRI | 2 | BELL & GOSSETT | 1510 SSF 10.625 2EB / C207033-01G51 | 65265368 / 65265369 |

TECHNICAL EXHIBIT 2 (TE-2)

AHUs Schedule

| Item Num | AHU Name | Location | Brand | Model # | Serial # |
| --- | --- | --- | --- | --- | --- |
| 1 | Air Handling Unit 1 | South Bed Tower | York | XTI-069X093-KAPA046A | CDTMX0009 |
| 2 | Air Handling Unit 2 | South Bed Tower | York | XTI-069X099-KAPA046A | CDTMXT0015 |
| 3 | Air Handling Unit 3 | South Bed Tower | York | XTI-069X093-KAPA046A | CDTMXT0011 |
| 4 | Air Handling Unit 4 | South Bed Tower | York | XTI-069X093-KAPA046A | CDTMXT0010 |
| 5 | Air Handling Unit 5 | South Bed Tower | York | XTI-072X102-KFPJ046A | CDTMXT0017 |
| 6 | Air Handling Unit 6 | South Bed Tower | York | XTI-078X108-KAQA046A | CDTMXT0016 |
| 7 | Air Handling Unit 7 | South Bed Tower | York | XTI-078X090-KFPJ046A | CDTMXT0168 |
| 8 | Air Handling Unit 8 | South Bed Tower | York | XTI-066X108-KAQA046A | CDTMXT0019 |
| 9 | Air Handling Unit 9 | South Bed Tower | York | XTI-069X093-KAPA046A | CDTMXT0014 |
| 10 | Air Handling Unit 10 | South Bed Tower | York | XTI-069X093-KAPA046A | CDTMXT0013 |
| 11 | Air Handling Unit 11 | South Bed Tower | York | XTI-069X093-KAPA046A | CDTMXT0012 |
| 12 | Air Handling Unit 12 | South Bed Tower | York | XTI-069X093-KAPA046A | CDTMXT0018 |
| 13 | Air Handling Unit 1 | Community Living Center | Trane | MCCB025UA0B0UA | K05B19250 |
| 14 | Air Handling Unit 2 | Community Living Center | Trane | MCCB035UA0B0UA | K0519255 |
| 15 | Air Handling Unit 3 | Community Living Center | Trane | MCCB0104UA0B0UA | K05B19262 |
| 16 | Air Handling Unit 4 | Community Living Center | Trane | MCCB0104UA0B0UA | K05B19267 |
| 17 | Air Handling Unit 5 | Community Living Center | Carrier | 39NT06-HDT | 2006500096 |
| 18 | Air Handling Unit 6 | Community Living Center | Carrier | 39NT06-HDT | 2006500097 |
| 19 | Air Handling Unit 1 SICU | Surgery Intensive Care Unit SICU | Carrier | 39NTR40-HDT | 200649O093 |
| 20 | Air Handling Unit 30 | Surgery Intensive Care Unit SICU | Trane | ****NO INFO***** | **NO INFO** |
| 21 | Air Handling Unit 32 | Surgery Intensive Care Unit SICU | Trane | ****NO INFO***** | **NO INFO** |
| 22 | Air Handling Unit 2 | Outpatient Admissions |  | CSAA021UAC00 | K11F69259 |
| 23 | Air Handling Unit Gastro | Outpatient Admissions | Trane | CSAA010UAL00 | H22C42333 |
| 24 | Air Handling Unit 100 | Outpatient Admissions | Trane | CSAA0044AC00 | K12E51434 |
| 25 | Air Handling Unit 23A, SPS | Building 1 | Engineering Products | TFMC-3030F | TF1904C5466 |
| 26 | Air Handling Unit 23B, SPS | Building 1 | Trane | CSOA035 |  |
| 27 | Inpatient Pharmacy Air Handling Unit 1 | Building 1 | Trane | CSAA010UAM00 | H23K90521 |
| 28 | Inpatient Pharmacy Air Handling Unit 2 | Building 1 | Trane | CSAA010UBL00 | K15E40349 |
| 29 | Linear Accelerator Air Handling Unit 1A | Building 1 | Trane | TSCB010U0C | K05B19297 |
| 30 | Linear Accelerator Air Handling Unit 1B | Building 1 | Trane | TSCB010U0C | K05B19291 |
| 31 | NEW Linear Accelerator Air Handling Unit | Building 1 |  | 0AH017FDAC | FB0U041000819 |
| 32 | Air Handling Unit 1A CT Scan | Building 1 | Trane | TSCA017N0C000000C00 | K0BKA3294A |
| 33 | Air Handling Unit 1B CT Scan | Building 1 | Trane | TSCA017N0C000000C00 | K10B15401 |
| 34 | Air Handling Unit CT/MRI 1A | Building 1 | Trane | TSCB010U0F000000000 AE00A12 | K10B15694 |
| 35 | Air Handling Unit CT/MRI 1B | Building 1 | Trane | TSCB01U0F0000000AC00A02 |  |
| 36 | Radio Therapy Air Handling Unit | Building 1 | York | BA0061220.00X048G06CB0165032WH122 | DHJM-080143 |
| 37 | Air Handling Unit 29 Morgue | Building 1 | Carrier | 39MN17W027JYB11X | 4720031812 |
| 38 | Air Handling Unit Foot Clinic | Building 1 | Carrier | 39MW03D021HZ511XCS | 0113U00500 |
| 39 | Air Handling Unit 18 Kitchen VCS | Building 1 | Trane | CSAA0084UAL00 | K16J72318 |
| 40 | Supply Fan Food and Nutrition 5R | Building 1 | Engineering Products | TFMC-2025F | TE1904C5470 |
| 41 | Air Handling Unit Cardio 101N | Building 1 | Engineering Products | TFMC-1520F | TF1904C5464 |
| 42 | Air Handling Unit Cardio Cath lab | Building 1 | Trane | CSAA006UBC00 | K12J07832A |
| 43 | Air Handling Unit Swimming Pool | Building 1 | Trane | TSCB010U0F00000000AC0AA206.5000 | K11F67638 |
| 44 | Air Handling Unit RTU 1 Operating Rooms | Building 1 | Trane | TSCB030D0F000 | K09B55992K |
| 45 | Air Handling Unit 2R Operating Rooms | Building 1 | Engineering Products | TFMC-3040F | TF1904C5462 |
| 46 | Supply Fan 1 A B9 Mechanical Room | Building 1 | Trane | TCCB056IDC0A0LTVVMVVF | C15B00889 |
| 47 | Supply Fan 1 B B9 Mechanical Room | Building 1 | Trane | TCCB024IDC0A0LTVVMVVF | C15B00890 |
| 48 | Supply Fan 1 C B9 Mechanical Room | Building 1 | Trane | TCCB101IDC0A0LTVVMVVF | C15B00891 |
| 49 | Air Handling Unit Interventional Radiology | Building 1 |  |  |  |
| 50 | Air Handling Unit 54 MSD | Building 1 |  |  |  |
| 51 | Air Handling Unit Nuclear Medicine A13 | Building 1 |  |  |  |

TECHNICAL EXHIBIT 3 (TE-3)

HEPA and V-Bank Air Filters

Filter Supply Requirements (Contract Line Item 0005 and Sub-Line Items 0005AA–0005AF)

| Type | Size | Estimated Quantities |
| --- | --- | --- |
| HEPA | 12” x 24” x 12” | 310 |
| HEPA | 24” x 30” x 12” | 430 |
| V-Bank | 24” x 24” x 12” | 1,240 |
| V-Bank | 20” x 24” x 12” | 500 |
| V-Bank | 20” x 20” x 12” | 280 |
| V-Bank | 12” x 24” x 12” | 540 |

TECHNICAL EXHIBIT 4 (TE-4)

Mapping of Contract Line Items (CLINs) to PWS Paragraphs

| CLIN | Description | Applicable PWS Paragraph |
| --- | --- | --- |
| 0001AA | Monthly Preventive Maintenance for Chillers, Pumps, and Associated Equipment | 3.1 (except those that are priced separately) |
| 0001AB | Semi-Annual Condenser Cleaning for water-cooled chillers | 3.1.3.3.1 |
| 0001AC | Annual Evaporator Mechanical Cleaning | 3.1.3.3.2 |
| 0001AD | Annual Oil Analysis and Related Maintenance | 3.1.3.2(d and e) |
| 0001AE | Annual Instrument Calibration (Gauges & Thermometers) | 3.1.3.2(l) |
| 0001AF | Major Overhaul of Centrifugal Compressors’ Assembly | 3.1.4 |
| 0001AG | Repair Work Beyond Standard PM Tasks - Chillers | 3.1.5 |
| 0002AA | Comprehensive Monthly Preventive Maintenance Services - AHUs | 3.2 (except those that are priced separately) |
| 0002AB | Repair Work Beyond Standard PM Tasks - AHUs | 3.2.5 |
| 0002AC | Replacement of Supply/Return Fan Assemblies | 3.2.3.3.6 |
| 0003AA | Ductwork Inspection and Leak Detection | 3.3.2.a |
| 0003AB | Sealing Duct Leaks | 3.3.2.b |
| 0003AC | Insulation Maintenance | 3.3.2.c |
| 0003AD | Ductwork Repairs and Section Replacement | 3.3.4.2 |
| 0003AE | System Upgrades (Ductwork Materials and Design) | 3.3.5.1 |
| 0003AF | New Installations (Duct Runs, Branches, and Components) | 3.3.5.2 |
| 0003AG | Dampers and Controls Installation | 3.3.5.3 |
| 0004 | Trailer-Mounted Chiller Contingency Support | 3.4., 3.4.1, 3.4.2 |
| 0005AA-0005AG | Filter Supply Requirements | 3.5 |

TECHNICAL EXHIBIT 5 (TE-5)

VA INFORMATION AND INFORMATION SYSTEM SECURITY/PRIVACY LANGUAGE

- VA INFORMATION CUSTODIAL LANGUAGE:

  - Contractors, contractor personnel, subcontractors, and subcontractor personnel shall be subject to the same Federal laws, regulations, standards, and VA Directives and Handbooks as VA and VA personnel regarding information and information system security.

  - If VA determines that the contractor has violated any of the information confidentiality, privacy, and security provisions of the contract, it shall be sufficient grounds for VA to withhold payment to the contractor or third party or terminate the contract for default or terminate for cause under Federal Acquisition Regulation (FAR) part 12.

  - A contractor/subcontractor shall request logical (technical) or physical access to VA information and VA information systems for their employees, subcontractors, and affiliates only to the extent necessary to perform the services specified in the contract, agreement, or task order.

  - All contractors, subcontractors, and third-party servicers and associates working with VA information are subject to the same investigative requirements as those of VA appointees or employees who have access to the same types of information. The level and process of background security investigations for contractors must be in accordance with VA Directive and Handbook 0710, Personnel Suitability and Security Program. The Office for Operations, Security, and Preparedness is responsible for these policies and procedures.

- SECURITY INCIDENT INVESTIGATION

  - The term “security incident” means an event that has, or could have, resulted in unauthorized access to, loss or damage to VA assets, or sensitive information, or an action that be A security procedures. The contractor/subcontractor shall immediately notify the PPOC and simultaneously, the designated ISO and Privacy Officer for the contract of any known or suspected security/privacy incidents, or any unauthorized disclosure of sensitive information, including that contained in system(s) to which the contractor/subcontractor has access.

  - To the extent known by the contractor/subcontractor, the contractor/subcontractor’s notice to VA shall identify the information involved, the circumstances surrounding the incident (including to whom, how, when, and where the VA information or assets were placed at risk or compromised), and any other information that the contractor/subcontractor considers relevant.

  - With respect to unsecured protected health information, the business associate is deemed to have discovered a data breach when the business associate knew or should have known of a breach of such information. Upon discovery, the business associate must notify the covered entity of the breach. Notifications need to be made in accordance with the executed business associate agreement.

  - In instances of theft or break-in or other criminal activity, the contractor/subcontractor must concurrently report the incident to the appropriate law enforcement entity (or entities) of jurisdiction, including the VA OIG and Security and Law Enforcement. The contractor, its employees, and its subcontractors and their employees shall cooperate with VA and any law enforcement authority responsible for the investigation and prosecution of any possible criminal law violation(s) associated with any incident. The contractor/subcontractor shall cooperate with VA in any civil litigation to recover VA information, obtain monetary or other compensation from a third party for damages arising from any incident, or obtain injunctive relief against any third party arising from, or related to, the incident.

- LIQUIDATED DAMAGES FOR DATA BREACH

  - Consistent with the requirements of 38 U.S.C. §5725, a contract may require access to sensitive personal information. If so, the contractor is liable to VA for liquidated damages in the event of a data breach or privacy incident involving any SPI the contractor/subcontractor processes or maintains under this contract. to be acceptable by VA, specifically to address mitigation of the resulting problems of communication, control, data protection, and so forth. Location within the U.S. may be an evaluation factor.

  - The contractor/subcontractor shall provide notice to VA of a “security incident” as set forth in the Security Incident Investigation section above. Upon such notification, VA must secure from a non-Department entity or the VA Office of Inspector General an independent risk analysis of the data breach to determine the level of risk associated with the data breach for the potential misuse of any sensitive personal information involved in the data breach. The term 'data breach' means the loss, theft, or other unauthorized access, or any access other than that incidental to the scope of employment, to data containing sensitive personal information, in electronic or printed form, that results in the potential compromise of the confidentiality or integrity of the data. Contractor shall fully cooperate with the entity performing the risk analysis. Failure to cooperate may be deemed a material breach and grounds for contract termination

- SECURITY CONTROLS COMPLIANCE TESTING

  - On a periodic basis, VA, including the Office of Inspector General, reserves the right to evaluate any or all of the security controls and privacy practices implemented by the contractor under the clauses contained within the contract. With 10 working-days’ notice, at the request of the government, the contractor must fully cooperate and assist in a government-sponsored security controls assessment at each location wherein VA information is processed or stored, or information systems are developed, operated, maintained, or used on behalf of VA, including those initiated by the Office of Inspector General. The government may conduct a security control assessment on shorter notice (to include unannounced assessments) as determined by VA in the event of a security incident or at any other time.

- TRAINING

  - All contractor employees and subcontractor employees requiring access to VA information and VA information systems shall complete VA Privacy and Information Security Awareness and Rules of Behavior Training before being granted access to VA information and its systems.

  - Sign and acknowledge (either manually or electronically) understanding of and responsibilities for compliance with the Rules of Behavior before being granted access to VA information and its systems.

  - The contractor shall provide to the contracting officer and/or the PPOC a copy of the training certificates and certification of signing the Rules of Behavior for each applicable employee within 1 week of the initiation of the contract and annually thereafter, as required.

  - Failure to complete the mandatory annual training and sign the Rules of Behavior annually, within the timeframe required, is grounds for suspension or termination of all physical or electronic access privileges and removal from work on the contract until such time as the training and documents are complete.