General Specifications

Table 1. The generators shall conform to the following technical specifications across all five RMP models:

| Parameter | 5 kW | 10 kW | 15 kW | 30 kW | 60 kW |
| --- | --- | --- | --- | --- | --- |
| Model | 5RMP-1030A | 10RMP-1040A/1041A | 15RMP-1050A/1051A | 30RMP-1060A/1061A | 60RMP-1070A/1071A |
| Power (60 Hz) | 5 kW | 10 kW | 15 kW | 30 kW | 60 kW |
| Power (50 Hz) | 5.2 kVA | 10.4 kVA | 15.6 kVA | 31 kVA | 62.5 kVA |
| Frequency | 50/60 Hz | 50/60/400 Hz | 50/60/400 Hz | 50/60/400 Hz | 50/60/400 Hz |
| Dimensions (L×W×H) | 45×32×36 in | 55×32×36 in | 65×36×53 in | 75×36×53 in | 82×36×53 in |
| Weight (dry) | 780 lbs (355 kg) | 1010 lbs (459 kg) | 1550 lbs (705 kg) | 2215 lbs (1007 kg) | 2985 lbs (1357 kg) |

https://www.cummins.com/en-na/generators/products/rugged-mobile-power

Table 2. Additional RMP Model Specifications

The Government’s minimum requirement for the 10 kW configuration is the Cummins Rugged Mobile Power (RMP) model 10RMP-1040A or 10RMP-1041A, or an equivalent Cummins RMP 10 kW configuration that has been subjected to and successfully passed HEMP survivability testing at NAWCAD Patuxent River or an equivalent formal DoD HEMP qualification program, with test results and certifications acceptable to the Government.

Common specifications for all models:

| Parameter | Specification |
| --- | --- |
| Manufacturer | Cummins Inc. (BRAND NAME OR EQUAL) |
| Military Standard | MIL-DTL-32496 |
| Fuel Type | Multi-fuel capable (JP-8, JP-4, DF-1, DF-2, DF-A) |
| Operating Environment | All environmental extremes (-50°F to 135°F) |
| EMC Compliance | MIL-STD-461F |

https://www.cummins.com/en-na/generators/products/rugged-mobile-power

Table 3: Common Technical Specifications (All Models)

Additional required features include:

- Rugged 4-cycle industrial diesel engine

- 24-volt starting system with NATO slave connection

- Nuclear, biological, and chemical (NBC) contamination survivability

- Battlefield mobility and ruggedized construction

- Low infrared and acoustic signatures

- Rated power output at altitude

- Automatic load control and voltage regulation (±3% no-load to full-load)