Specifications / Scope

Task: Procurement of Replacement Wastewater and Hazardous Solids Handling Lift Station Pump

For Flagg Ranch Lift Station

Grand Teton National Park

Table of Contents

1.0    Project Description / Summary

2.0    Objectives

3.0    Background

4.0    Specific Work / Tasks

5.0   Optional Work / Tasks

6.0    Government Furnished Equipment / Materials / Other

7.0    Special Conditions / Requirements

8.0    Place of Performance

9.0    Performance Period / Schedule Requirements

- Project Description / Summary: 
This project shall procure and deliver to Grand Teton National Park a specific Hazardous Solids Handling Wastewater Pump for an existing lift station.  Pump specifications shall match exactly as specified herein in order to operate with existing lift station controls and communication networks along with existing power requirements and size for fit within the lift station.

- Objectives: 
The purpose of this project is to purchase one new lift station pump to replace one of the two existing pumps that has failed.

- Specific Tasks:

  - Successful bidder for this project shall provide one new replacement pump meeting the following specifications, and shall deliver the new pump to Grand Teton National Park at the provided shipping location of Moose Warehouse, Grand Teton National Park  103 Headquarters Loop  Moose WY, 83012, C/O Patrick Larson

    - Specifications: specifications shall be required to be exact brand specific in order to match the existing lift station configuration, power requirements, and controller requirements.  This product is intended to be a match to the existing lift station pump and the replacement pump (existing lift station is set up as a redundant pump system with two identical pumps running in sequence)

      - Pump shall be as follows:

      - Myers 4VHX75M4-03 Hazardous Solids Handling Wastewater Pump –

      - Model: Myers 4VHX75M4-03 Hazardous Solids Handling Wastewater Pump

      - Motor / Power:

      - 7.5 HP

      - 3-phase, 200V, 60 Hz

      - Full load amps: 30

      - Oil-filled motor for maximum heat dissipation and constant bearing lubrication

      - RPM: 1750

      - Heat sensor for motor over-temperature protection (auto reset)

      - Hydraulic Performance:  Maximum head: 85 ft

      - Maximum capacity: 725 GPM

      - Maximum liquid temperature: 140°F (60°C)

      - Switch type: Manual

      - Solids Handling & Pumping Capability:  Capable of passing full 3" spherical solids

      - Designed for hazardous solids wastewater environments

      - Modified constant-velocity volute for smooth performance and long seal/bearing life

      - Impeller & Internal Components:  Impeller: Ductile iron enclosed 2-vane with rounded ports

      - Optional single-vane impeller available

      - Pump-out vanes reduce seal face pressure and keep debris away from seal

      - Brass wear ring to prevent rust buildup and maintain clearances

      - Sleeve bearing absorbs radial shock loads

      - Heavy 416 stainless steel shaft (corrosion resistant)

      - Seals & Motor Protection:

      - Double tandem mechanical shaft seals

      - Oil-filled seal chamber for constant lubrication

      - Seal leak probes detect water in seal housing and trigger warning in control panel

      - Cable entry system with compression grommet + epoxy-potted conductor sealing (double protection)

      - Construction:

      - Body construction: Cast iron

      - Discharge: 4" 125-lb ANSI flange

      - Cord size: 8-4; W

      - Robust construction for municipal, industrial, and lift-station applications

      - Hazardous Duty Rating:

      - UL Listed for Class I, Division 1, Group D hazardous locations

      - CONTROL BOX REQUIRED (not included)

      - Typical Applications:

      - Municipal lift stations

      - Wastewater treatment plants

      - Industrial wastewater systems

- Special Conditions / Requirements:

  - New pump shall be only as approved by the CO

- Place Of Performance:

  - Grand Teton National Park –

- Performance Period / Schedule Requirements:

  - New pump shall be delivered to Grand Teton National Park no later than 5/1/2026